## Data
|  |  | Evt Detect |  |  | Low Delt Hz | Hi Delt Hz
|  |  | Row | 60 | 0.114 | -0.114 | 0.021 | 1
|  |  | 160 | 40626.5827 | t(0)
|  |  | 270 | 40626.5853 | t(Recovery)
Time (T) | Hz | MW | 161 | 0:04 | Event Length mm:ss
40626.5792 | 60.024 | 548.8694 |  | 0
40626.5792 | 60.024 | 548.848 | 0 | 0 | 0 | 0 | 0
40626.5792 | 60.026 | 548.848 | 0 | 0 | 0 | 0.0020027 | 0.0020027
40626.5792 | 60.022 | 548.3702 | 0 | 0 | 0 | -0.0040016 | 0.0040016
40626.5793 | 60.023 | 548.3702 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5793 | 60.026 | 548.655 | 0 | 0 | 0 | 0.0030022 | 0.0030022
40626.5793 | 60.027 | 548.655 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5793 | 60.028 | 548.1422 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5794 | 60.027 | 548.1422 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5794 | 60.026 | 548.407 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5794 | 60.025 | 548.407 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5794 | 60.029 | 548.4528 | 0 | 0 | 0 | 0.0039978 | 0.0039978
40626.5794 | 60.028 | 548.4528 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5795 | 60.031 | 548.9803 | 0 | 0 | 0 | 0.0029984 | 0.0029984
40626.5795 | 60.031 | 548.9803 | 0 | 0 | 0 | 0 | 0
40626.5795 | 60.027 | 548.5504 | 0 | 0 | 0 | -0.0039978 | 0.0039978
40626.5795 | 60.024 | 548.5504 | 0 | 0 | 0 | -0.0030022 | 0.0030022
40626.5796 | 60.024 | 547.4811 | 0 | 0 | 0 | 0 | 0
40626.5796 | 60.021 | 547.4811 | 0 | 0 | 0 | -0.0029984 | 0.0029984
40626.5796 | 60.019 | 548.8652 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.5796 | 60.019 | 548.8652 | 0 | 0 | 0 | 0 | 0
40626.5797 | 60.018 | 548.5429 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5797 | 60.02 | 548.5429 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.5797 | 60.022 | 547.1166 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.5797 | 60.021 | 547.1166 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5797 | 60.022 | 546.1401 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5798 | 60.02 | 546.1401 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.5798 | 60.021 | 547.5071 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5798 | 60.019 | 547.5071 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.5798 | 60.018 | 547.8394 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5799 | 60.018 | 547.8394 | 0 | 0 | 0 | 0 | 0
40626.5799 | 60.018 | 549.3954 | 0 | 0 | 0 | 0 | 0
40626.5799 | 60.018 | 549.3954 | 0 | 0 | 0 | 0 | 0
40626.5799 | 60.023 | 550.7976 | 0 | 0 | 0 | 0.0049973 | 0.0049973
40626.58 | 60.021 | 550.7976 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.58 | 60.013 | 550.3647 | 0 | 0 | 0 | -0.0079994 | 0.0079994
40626.58 | 60.008 | 550.3647 | 0 | 0 | 0 | -0.0050011 | 0.0050011
40626.58 | 60.006 | 549.6343 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.58 | 60.002 | 549.6343 | 0 | 0 | 0 | -0.0040016 | 0.0040016
40626.5801 | 59.998 | 549.7502 | 0 | 0 | 0 | -0.0039978 | 0.0039978
40626.5801 | 59.993 | 550.3429 | 0 | 0 | 0 | -0.0050011 | 0.0050011
40626.5801 | 59.99 | 550.4783 | 0 | 0 | 0 | -0.0029984 | 0.0029984
40626.5801 | 59.992 | 550.4783 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.5802 | 59.994 | 550.337 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.5802 | 59.997 | 550.337 | 0 | 0 | 0 | 0.0030022 | 0.0030022
40626.5802 | 60.014 | 550.1797 | 0 | 0 | 0 | 0.016998 | 0.016998
40626.5802 | 60.023 | 550.1797 | 0 | 0 | 0 | 0.0089989 | 0.0089989
40626.5803 | 60.03 | 551.1789 | 0 | 0 | 0 | 0.007 | 0.007
40626.5803 | 60.033 | 551.1789 | 0 | 0 | 0 | 0.0030022 | 0.0030022
40626.5803 | 60.034 | 550.9922 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5803 | 60.036 | 550.9922 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.5803 | 60.032 | 551.5048 | 0 | 0 | 0 | -0.0039978 | 0.0039978
40626.5804 | 60.034 | 551.5048 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.5804 | 60.036 | 551.5916 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.5804 | 60.034 | 551.5916 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.5804 | 60.042 | 549.355 | 0 | 0 | 0 | 0.0079994 | 0.0079994
40626.5805 | 60.043 | 549.355 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5805 | 60.042 | 547.3488 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5805 | 60.036 | 547.3488 | 0 | 0 | 0 | -0.0060005 | 0.0060005
40626.5805 | 60.039 | 548.9902 | 0 | 0 | 0 | 0.0030022 | 0.0030022
40626.5806 | 60.04 | 548.9902 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5806 | 60.043 | 548.5718 | 0 | 0 | 0 | 0.0029984 | 0.0029984
40626.5806 | 60.045 | 548.5718 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.5806 | 60.047 | 548.8831 | 0 | 0 | 0 | 0.0020027 | 0.0020027
40626.5806 | 60.047 | 548.8831 | 0 | 0 | 0 | 0 | 0
40626.5807 | 60.047 | 548.4909 | 0 | 0 | 0 | 0 | 0
40626.5807 | 60.046 | 548.4909 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5807 | 60.046 | 547.9343 | 0 | 0 | 0 | 0 | 0
40626.5807 | 60.043 | 547.9343 | 0 | 0 | 0 | -0.0030022 | 0.0030022
40626.5808 | 60.041 | 548.6513 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.5808 | 60.042 | 548.6513 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5808 | 60.041 | 547.906 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5808 | 60.042 | 547.906 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5809 | 60.045 | 547.6615 | 0 | 0 | 0 | 0.0029984 | 0.0029984
40626.5809 | 60.041 | 547.6615 | 0 | 0 | 0 | -0.0039978 | 0.0039978
40626.5809 | 60.035 | 547.0771 | 0 | 0 | 0 | -0.0060005 | 0.0060005
40626.5809 | 60.036 | 547.0771 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5809 | 60.036 | 546.8329 | 0 | 0 | 0 | 0 | 0
40626.581 | 60.034 | 546.8329 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.581 | 60.039 | 546.6302 | 0 | 0 | 0 | 0.0050011 | 0.0050011
40626.581 | 60.041 | 546.6302 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.581 | 60.039 | 545.5642 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.5811 | 60.039 | 545.5642 | 0 | 0 | 0 | 0 | 0
40626.5811 | 60.04 | 544.636 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5811 | 60.035 | 544.636 | 0 | 0 | 0 | -0.0050011 | 0.0050011
40626.5811 | 60.032 | 543.7035 | 0 | 0 | 0 | -0.0029984 | 0.0029984
40626.5812 | 60.032 | 543.7035 | 0 | 0 | 0 | 0 | 0
40626.5812 | 60.029 | 543.5815 | 0 | 0 | 0 | -0.0030022 | 0.0030022
40626.5812 | 60.028 | 543.5815 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5812 | 60.025 | 543.227 | 0 | 0 | 0 | -0.0029984 | 0.0029984
40626.5813 | 60.024 | 543.227 | 0 | 0 | 0 | -0.0010033 | 0.0010033
40626.5813 | 60.024 | 542.2418 | 0 | 0 | 0 | 0 | 0
40626.5813 | 60.024 | 542.2418 | 0 | 0 | 0 | 0 | 0
40626.5813 | 60.024 | 540.9113 | 0 | 0 | 0 | 0 | 0
40626.5813 | 60.025 | 540.9113 | 0 | 0 | 0 | 0.0010033 | 0.0010033
40626.5814 | 60.027 | 540.4435 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.5814 | 60.027 | 540.4435 | 0 | 0 | 0 | 0 | 0
40626.5814 | 60.024 | 540.0917 | 0 | 0 | 0 | -0.0030022 | 0.0030022
40626.5814 | 60.025 | 540.0917 | 0 | 0 | 0 | 0.0010033 | 0.0010033
40626.5815 | 60.027 | 538.3438 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.5815 | 60.027 | 538.3438 | 0 | 0 | 0 | 0 | 0
40626.5815 | 60.025 | 537.4531 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.5815 | 60.024 | 537.4531 | 0 | 0 | 0 | -0.0010033 | 0.0010033
40626.5816 | 60.023 | 536.5582 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5816 | 60.023 | 536.5582 | 0 | 0 | 0 | 0 | 0
40626.5816 | 60.022 | 537.2059 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5816 | 60.018 | 537.2059 | 0 | 0 | 0 | -0.0039978 | 0.0039978
40626.5816 | 60.014 | 538.1455 | 0 | 0 | 0 | -0.0040016 | 0.0040016
40626.5817 | 60.008 | 538.1455 | 0 | 0 | 0 | -0.0060005 | 0.0060005
40626.5817 | 60.007 | 538.0366 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5817 | 60.004 | 538.0366 | 0 | 0 | 0 | -0.0029984 | 0.0029984
40626.5817 | 60.002 | 537.86 | 0 | 0 | 0 | -0.0020027 | 0.0020027
40626.5818 | 60.003 | 537.86 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5818 | 60.004 | 537.0419 | 0 | 0 | 0 | 0.0010033 | 0.0010033
40626.5818 | 60.006 | 537.0419 | 0 | 0 | 0 | 0.0019989 | 0.0019989
40626.5818 | 60.01 | 537.14 | 0 | 0 | 0 | 0.0039978 | 0.0039978
40626.5819 | 60.013 | 537.14 | 0 | 0 | 0 | 0.0030022 | 0.0030022
40626.5819 | 60.012 | 535.7023 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5819 | 60.013 | 535.7023 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5819 | 60.012 | 534.7816 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5819 | 60.013 | 534.7816 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.582 | 60.013 | 535.0607 | 0 | 0 | 0 | 0 | 0
40626.582 | 60.013 | 535.0607 | 0 | 0 | 0 | 0 | 0
40626.582 | 60.013 | 535.4227 | 0 | 0 | 0 | 0 | 0
40626.582 | 60.028 | 535.4227 | 0 | 0 | 0 | 0.014999 | 0.014999
40626.5821 | 60.035 | 534.8942 | 0 | 0 | 0 | 0.007 | 0.007
40626.5821 | 60.039 | 534.8942 | 0 | 0 | 0 | 0.0040016 | 0.0040016
40626.5821 | 60.039 | 536.0845 | 0 | 0 | 0 | 0 | 0
40626.5821 | 60.038 | 536.0845 | 0 | 0 | 0 | -0.0010033 | 0.0010033
40626.5822 | 60.031 | 534.3259 | 0 | 0 | 0 | -0.007 | 0.007
40626.5822 | 60.031 | 534.3259 | 0 | 0 | 0 | 0 | 0
40626.5822 | 60.029 | 534.3387 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.5822 | 60.028 | 534.3387 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5822 | 60.028 | 534.5214 | 0 | 0 | 0 | 0 | 0
40626.5823 | 60.029 | 534.5214 | 0 | 0 | 0 | 0.00099945 | 0.00099945
40626.5823 | 60.028 | 533.7285 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5823 | 60.028 | 533.7285 | 0 | 0 | 0 | 0 | 0
40626.5823 | 60.028 | 533.5816 | 0 | 0 | 0 | 0 | 0
40626.5824 | 60.031 | 533.5816 | 0 | 0 | 0 | 0.0029984 | 0.0029984
40626.5824 | 60.03 | 532.539 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5824 | 60.028 | 532.539 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.5824 | 60.027 | 532.505 | 0 | 0 | 0 | -0.00099945 | 0.00099945
40626.5825 | 60.03 | 532.505 | 0 | 0 | 0 | 0.0029984 | 0.0029984
40626.5825 | 60.025 | 531.8575 | 0 | 0 | 0 | -0.0049973 | 0.0049973
40626.5825 | 60.019 | 531.8575 | 0 | 0 | 0 | -0.0060005 | 0.0060005
40626.5825 | 60.016 | 531.4795 | 0 | 0 | 0 | -0.0030022 | 0.0030022
40626.5825 | 60.011 | 531.4795 | 0 | 0 | 0 | -0.0049973 | 0.0049973
40626.5826 | 60.008 | 530.5207 | 0 | 0 | 0 | -0.0030022 | 0.0030022
40626.5826 | 60.006 | 530.5207 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.5826 | 60.003 | 528.7762 | 0 | 0 | 0 | -0.0030022 | 0.0030022
40626.5826 | 60 | 528.7762 | 0 | 0 | 0 | -0.0029984 | 0.0029984
40626.5827 | 59.998 | 530.5581 | 0 | 0 | 0 | -0.0019989 | 0.0019989
40626.5827 | 59.996 | 530.5581 | 0 | 0 | 0 | -0.0020027 | 0.0020027
40626.5827 | 59.997 | 529.7286 | 0 | 0 | 0 | 0.0010033 | 0.0010033
40626.5827 | 59.977 | 529.7286 | 0 | 0 | 1 | -0.02 | 0.02
40626.5828 | 59.863 | 529.7286 | 1 | 0 | 1 | -0.114 | 0.114
40626.5828 | 59.814 | 530.0621 | 1 | 0 | 1 | -0.049 | 0.049
40626.5828 | 59.799 | 534.4206 | 1 | 0 | 1 | -0.014999 | 0.014999
40626.5828 | 59.799 | 534.4206 | 1 | 0 | 1 | 0 | 0
40626.5828 | 59.801 | 544.002 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5829 | 59.8 | 544.002 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5829 | 59.803 | 548.178 | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5829 | 59.808 | 548.178 | 1 | 0 | 1 | 0.0049973 | 0.0049973
40626.5829 | 59.81 | 546.6487 | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.583 | 59.817 | 546.6487 | 1 | 0 | 1 | 0.007 | 0.007
40626.583 | 59.824 | 544.5483 | 1 | 0 | 1 | 0.007 | 0.007
40626.583 | 59.824 | 544.5483 | 1 | 0 | 1 | 0 | 0
40626.583 | 59.827 | 541.8083 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5831 | 59.827 | 541.8083 | 1 | 0 | 1 | 0 | 0
40626.5831 | 59.828 | 539.9456 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5831 | 59.826 | 539.9456 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5831 | 59.823 | 541.4998 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5831 | 59.824 | 541.4998 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5832 | 59.822 | 543.3224 | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.5832 | 59.818 | 543.3224 | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.5832 | 59.818 | 545.1118 | 1 | 0 | 1 | 0 | 0
40626.5832 | 59.815 | 545.1118 | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.5833 | 59.812 | 545.9412 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5833 | 59.815 | 545.9412 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5833 | 59.82 | 545.9116 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5833 | 59.819 | 545.9116 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5834 | 59.819 | 544.8771 | 1 | 0 | 1 | 0 | 0
40626.5834 | 59.819 | 544.8771 | 1 | 0 | 1 | 0 | 0
40626.5834 | 59.821 | 544.639 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5834 | 59.825 | 544.639 | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5834 | 59.83 | 545.9454 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5835 | 59.831 | 545.9454 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5835 | 59.839 | 544.6492 | 1 | 0 | 1 | 0.0079994 | 0.0079994
40626.5835 | 59.839 | 544.6492 | 1 | 0 | 1 | 0 | 0
40626.5835 | 59.842 | 543.997 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5836 | 59.847 | 543.997 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5836 | 59.846 | 544.2888 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5836 | 59.845 | 544.2888 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5836 | 59.846 | 544.4759 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5837 | 59.85 | 544.4759 | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.5837 | 59.85 | 545.1849 | 1 | 0 | 1 | 0 | 0
40626.5837 | 59.854 | 545.1849 | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5837 | 59.863 | 543.7529 | 1 | 0 | 1 | 0.0089989 | 0.0089989
40626.5837 | 59.867 | 543.7529 | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5838 | 59.867 | 543.9365 | 1 | 0 | 1 | 0 | 0
40626.5838 | 59.874 | 543.9365 | 1 | 0 | 1 | 0.007 | 0.007
40626.5838 | 59.875 | 542.6066 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5838 | 59.881 | 542.6066 | 1 | 0 | 1 | 0.0060005 | 0.0060005
40626.5839 | 59.881 | 542.5233 | 1 | 0 | 1 | 0 | 0
40626.5839 | 59.887 | 542.5233 | 1 | 0 | 1 | 0.0060005 | 0.0060005
40626.5839 | 59.891 | 544.5529 | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.5839 | 59.902 | 544.5529 | 1 | 0 | 1 | 0.011002 | 0.011002
40626.584 | 59.9 | 545.1033 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.584 | 59.9 | 545.1033 | 1 | 0 | 1 | 0 | 0
40626.584 | 59.899 | 545.5423 | 1 | 0 | 1 | -0.0010033 | 0.0010033
40626.584 | 59.899 | 545.5423 | 1 | 0 | 1 | 0 | 0
40626.5841 | 59.902 | 546.4443 | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5841 | 59.912 | 546.4443 | 1 | 0 | 1 | 0.0099983 | 0.0099983
40626.5841 | 59.918 | 547.3142 | 1 | 0 | 1 | 0.0060005 | 0.0060005
40626.5841 | 59.918 | 547.3142 | 1 | 0 | 1 | 0 | 0
40626.5841 | 59.918 | 547.3142 | 1 | 0 | 1 | 0 | 0
40626.5842 | 59.923 | 548.6801 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5842 | 59.926 | 548.4333 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5842 | 59.924 | 548.4333 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5842 | 59.928 | 549.0335 | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5843 | 59.93 | 549.0335 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5843 | 59.93 | 549.2899 | 1 | 0 | 1 | 0 | 0
40626.5843 | 59.931 | 549.2899 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5843 | 59.933 | 550.1923 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5844 | 59.936 | 550.1923 | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5844 | 59.935 | 550.5021 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5844 | 59.938 | 550.5021 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5844 | 59.94 | 551.5063 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5844 | 59.938 | 551.5063 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5845 | 59.938 | 552.3267 | 1 | 0 | 1 | 0 | 0
40626.5845 | 59.938 | 552.3267 | 1 | 0 | 1 | 0 | 0
40626.5845 | 59.943 | 552.3267 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5845 | 59.945 | 552.2819 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5846 | 59.945 | 551.3163 | 1 | 0 | 1 | 0 | 0
40626.5846 | 59.944 | 551.3163 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5846 | 59.946 | 550.5966 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5846 | 59.951 | 550.5966 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5847 | 59.953 | 549.5225 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5847 | 59.954 | 549.5225 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5847 | 59.959 | 551.1065 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5847 | 59.962 | 551.1065 | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5847 | 59.964 | 550.8215 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5848 | 59.964 | 550.8215 | 1 | 0 | 1 | 0 | 0
40626.5848 | 59.963 | 551.5969 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5848 | 59.963 | 551.5969 | 1 | 0 | 1 | 0 | 0
40626.5848 | 59.965 | 552.2954 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5849 | 59.967 | 552.2954 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5849 | 59.97 | 552.7968 | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5849 | 59.971 | 552.7968 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5849 | 59.972 | 552.5348 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.585 | 59.97 | 552.5348 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.585 | 59.972 | 552.3873 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.585 | 59.974 | 552.3873 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.585 | 59.975 | 553.2163 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.585 | 59.975 | 553.2163 | 1 | 0 | 1 | 0 | 0
40626.5851 | 59.976 | 551.8028 | 1 | 0 | 1 | 0.0010033 | 0.0010033
40626.5851 | 59.977 | 551.8028 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5851 | 59.978 | 551.3834 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5851 | 59.981 | 551.3834 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5852 | 59.983 | 552.4021 | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.5852 | 59.985 | 552.4021 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5852 | 59.991 | 551.3555 | 1 | 0 | 1 | 0.0060005 | 0.0060005
40626.5852 | 59.991 | 551.3555 | 1 | 0 | 1 | 0 | 0
40626.5853 | 59.996 | 552.7619 | 1 | 0 | 1 | 0.0049973 | 0.0049973
40626.5853 | 60.002 | 552.7619 | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.5853 | 60.004 | 551.6282 | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.5853 | 60.005 | 551.6282 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5853 | 60.008 | 553.1126 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5854 | 60.014 | 553.1126 | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.5854 | 60.019 | 554.8657 | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.5854 | 60.022 | 554.8657 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5854 | 60.029 | 553.5314 | 1 | 1 | 1 | 0.007 | 0.007
40626.5855 | 60.033 | 553.5314 | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5855 | 60.038 | 554.5707 | 1 | 1 | 1 | 0.0049973 | 0.0049973
40626.5855 | 60.034 | 554.5707 | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.5855 | 60.037 | 552.4359 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5856 | 60.039 | 552.4359 | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.5856 | 60.039 | 549.1614 | 1 | 1 | 1 | 0 | 0
40626.5856 | 60.042 | 549.1614 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5856 | 60.041 | 547.9406 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5856 | 60.043 | 547.9406 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5857 | 60.041 | 549.3499 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5857 | 60.043 | 549.3499 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5857 | 60.044 | 548.9299 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5857 | 60.046 | 548.9299 | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.5858 | 60.043 | 549.8917 | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5858 | 60.038 | 549.8917 | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.5858 | 60.039 | 550.0666 | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.5858 | 60.037 | 550.0666 | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5859 | 60.034 | 550.5659 | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.5859 | 60.036 | 550.5659 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5859 | 60.034 | 550.2272 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5859 | 60.036 | 550.2272 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5859 | 60.035 | 551.4907 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.586 | 60.033 | 551.4907 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.586 | 60.039 | 551.1985 | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.586 | 60.041 | 551.1985 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.586 | 60.038 | 551.0989 | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5861 | 60.034 | 551.0989 | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.5861 | 60.031 | 551.5338 | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5861 | 60.026 | 551.5338 | 1 | 1 | 1 | -0.0049973 | 0.0049973
40626.5861 | 60.027 | 551.2632 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5862 | 60.026 | 551.2632 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5862 | 60.026 | 550.0291 | 1 | 1 | 1 | 0 | 0
40626.5862 | 60.024 | 550.0291 | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5862 | 60.026 | 549.8652 | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.5863 | 60.025 | 549.8652 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5863 | 60.024 | 550.7635 | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.5863 | 60.029 | 550.7635 | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.5863 | 60.036 | 549.9413 | 1 | 1 | 1 | 0.007 | 0.007
40626.5863 | 60.04 | 549.9413 | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5864 | 60.046 | 549.524 | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.5864 | 60.048 | 549.524 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5864 | 60.047 | 548.0062 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5864 | 60.046 | 548.0062 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5865 | 60.044 | 547.0096 | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5865 | 60.047 | 547.0096 | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5865 | 60.046 | 546.6521 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5865 | 60.047 | 546.6521 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5866 | 60.047 | 546.4784 | 1 | 1 | 1 | 0 | 0
40626.5866 | 60.047 | 546.4784 | 1 | 1 | 1 | 0 | 0
40626.5866 | 60.046 | 547.623 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5866 | 60.049 | 547.623 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5866 | 60.05 | 548.4683 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5867 | 60.049 | 548.4683 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5867 | 60.047 | 548.267 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5867 | 60.043 | 548.267 | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5867 | 60.042 | 545.7502 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5868 | 60.038 | 545.7502 | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5868 | 60.038 | 547.5976 | 1 | 1 | 1 | 0 | 0
40626.5868 | 60.036 | 547.5976 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5868 | 60.033 | 546.1004 | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.5869 | 60.031 | 546.1004 | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5869 | 60.035 | 545.7265 | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5869 | 60.037 | 545.7265 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5869 | 60.04 | 545.4362 | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5869 | 60.039 | 545.4362 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.587 | 60.038 | 545.7387 | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.587 | 60.036 | 545.7387 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.587 | 60.032 | 545.1893 | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.587 | 60.03 | 545.1893 | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5871 | 60.03 | 546.3142 | 1 | 1 | 1 | 0 | 0
40626.5871 | 60.029 | 546.3142 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5871 | 60.032 | 545.6485 | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5871 | 60.032 | 545.6485 | 1 | 1 | 1 | 0 | 0
40626.5872 | 60.03 | 545.5865 | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5872 | 60.032 | 545.5865 | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.5872 | 60.029 | 543.9636 | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5872 | 60.026 | 543.9636 | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.5872 | 60.025 | 543.4549 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5873 | 60.02 | 543.4549 | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.5873 | 60.023 | 542.8652 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5873 | 60.016 | 542.8652 | 1 | 1 | 1 | -0.007 | 0.007
40626.5873 | 60.012 | 543.6949 | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.5874 | 60.011 | 543.6949 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5874 | 60.01 | 543.2955 | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.5874 | 60.008 | 543.2955 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5874 | 60.01 | 543.6184 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5875 | 60.011 | 543.8499 | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.5875 | 60.012 | 543.8499 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5875 | 60.014 | 543.8499 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5875 | 60.016 | 543.7864 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5875 | 60.018 | 543.7864 | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.5876 | 60.018 | 543.9342 | 1 | 1 | 1 | 0 | 0
40626.5876 | 60.02 | 543.9342 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5876 | 60.018 | 544.7661 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5876 | 60.017 | 544.7661 | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.5877 | 60.017 | 544.2815 | 1 | 1 | 1 | 0 | 0
40626.5877 | 60.017 | 544.998 | 1 | 1 | 1 | 0 | 0
40626.5877 | 60.016 | 544.998 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5877 | 60.018 | 544.998 | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.5878 | 60.022 | 544.2836 | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.5878 | 60.023 | 544.2836 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5878 | 60.022 | 543.6278 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5878 | 60.033 | 543.6278 | 1 | 1 | 1 | 0.011002 | 0.011002
40626.5878 | 60.042 | 542.7296 | 1 | 1 | 1 | 0.0089989 | 0.0089989
40626.5879 | 60.052 | 542.7296 | 1 | 1 | 1 | 0.0099983 | 0.0099983
40626.5879 | 60.048 | 541.7638 | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.5879 | 60.044 | 541.7638 | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5879 | 60.042 | 540.6999 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.588 | 60.041 | 540.6999 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.588 | 60.044 | 540.5129 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.588 | 60.042 | 540.5129 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.588 | 60.042 | 541.0801 | 1 | 1 | 1 | 0 | 0
40626.5881 | 60.041 | 541.0801 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5881 | 60.038 | 540.7869 | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5881 | 60.037 | 540.7869 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5881 | 60.036 | 541.9575 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5881 | 60.041 | 541.9575 | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.5882 | 60.036 | 540.6132 | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.5882 | 60.037 | 540.6132 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5882 | 60.037 | 540.6246 | 1 | 1 | 1 | 0 | 0
40626.5882 | 60.036 | 540.6246 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5883 | 60.035 | 541.1522 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5883 | 60.034 | 541.1522 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5883 | 60.032 | 540.2507 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5883 | 60.035 | 540.2507 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5884 | 60.037 | 539.8033 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5884 | 60.037 | 539.8033 | 1 | 1 | 1 | 0 | 0
40626.5884 | 60.035 | 539.3864 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5884 | 60.035 | 539.3864 | 1 | 1 | 1 | 0 | 0
40626.5884 | 60.032 | 539.1969 | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.5885 | 60.037 | 539.1969 | 1 | 1 | 1 | 0.0049973 | 0.0049973
40626.5885 | 60.036 | 539.8394 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5885 | 60.041 | 539.8394 | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.5885 | 60.04 | 539.6266 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5886 | 60.038 | 539.6266 | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5886 | 60.037 | 540.0292 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5886 | 60.04 | 540.0292 | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5886 | 60.039 | 537.6292 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5887 | 60.036 | 537.6292 | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5887 | 60.039 | 538.2805 | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5887 | 60.037 | 538.2805 | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5887 | 60.035 | 539.3442 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5888 | 60.032 | 539.3442 | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.5888 | 60.033 | 539.9172 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5888 | 60.035 | 539.9172 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5888 | 60.034 | 539.979 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5888 | 60.033 | 539.979 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5889 | 60.036 | 539.7486 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5889 | 60.033 | 539.7486 | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.5889 | 60.033 | 540.1162 | 1 | 1 | 1 | 0 | 0
40626.5889 | 60.032 | 540.1162 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.589 | 60.027 | 540.6266 | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.589 | 60.025 | 540.6266 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.589 | 60.025 | 540.9314 | 1 | 1 | 1 | 0 | 0
40626.589 | 60.014 | 540.9314 | 1 | 1 | 1 | -0.011002 | 0.011002
40626.5891 | 60.014 | 541.9986 | 1 | 1 | 1 | 0 | 0
40626.5891 | 60.005 | 541.9986 | 1 | 1 | 1 | -0.0089989 | 0.0089989
40626.5891 | 60 | 541.3756 | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.5891 | 59.994 | 541.3756 | 1 | 0 | 1 | -0.0060005 | 0.0060005
40626.5891 | 59.977 | 543.6105 | 1 | 0 | 1 | -0.016998 | 0.016998
40626.5892 | 59.973 | 543.6105 | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.5892 | 59.97 | 544.2067 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5892 | 59.97 | 544.2067 | 1 | 0 | 1 | 0 | 0
40626.5892 | 59.968 | 545.4058 | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.5893 | 59.969 | 545.4058 | 1 | 0 | 1 | 0.0010033 | 0.0010033
40626.5893 | 59.969 | 547.0699 | 1 | 0 | 1 | 0 | 0
40626.5893 | 59.965 | 547.0699 | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.5893 | 59.964 | 547.2808 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5894 | 59.964 | 547.2808 | 1 | 0 | 1 | 0 | 0
40626.5894 | 59.97 | 549.0167 | 1 | 0 | 1 | 0.0060005 | 0.0060005
40626.5894 | 59.969 | 549.0167 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5894 | 59.971 | 551.0373 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5894 | 59.974 | 551.0373 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5895 | 59.975 | 551.6588 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5895 | 59.976 | 551.6588 | 1 | 0 | 1 | 0.0010033 | 0.0010033
40626.5895 | 59.977 | 551.348 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5895 | 59.977 | 551.348 | 1 | 0 | 1 | 0 | 0
40626.5896 | 59.976 | 550.2926 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5896 | 59.973 | 550.2926 | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.5896 | 59.975 | 551.9522 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5896 | 59.977 | 551.9522 | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.5897 | 59.973 | 552.2561 | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.5897 | 59.969 | 552.2561 | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.5897 | 59.966 | 552.5391 | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.5897 | 59.966 | 552.5391 | 1 | 0 | 1 | 0 | 0
40626.5897 | 59.965 | 552.8584 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5898 | 59.965 | 552.8584 | 1 | 0 | 1 | 0 | 0
40626.5898 | 59.968 | 554.4174 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5898 | 59.964 | 554.4174 | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.5898 | 59.964 | 554.3207 | 1 | 0 | 1 | 0 | 0
40626.5899 | 59.966 | 554.3207 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5899 | 59.971 | 553.5225 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5899 | 59.973 | 553.5225 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5899 | 59.975 | 553.7564 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.59 | 59.979 | 553.7564 | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.59 | 59.981 | 552.7703 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.59 | 59.983 | 552.7703 | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.59 | 59.98 | 554.7769 | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.59 | 59.979 | 554.7769 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5901 | 59.982 | 555.6833 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5901 | 59.987 | 555.6833 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5901 | 59.994 | 554.7871 | 1 | 0 | 1 | 0.007 | 0.007
40626.5901 | 59.998 | 554.7871 | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5902 | 59.997 | 556.4283 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5902 | 59.996 | 556.4283 | 1 | 0 | 1 | -0.0010033 | 0.0010033
40626.5902 | 59.996 | 554.0075 | 1 | 0 | 1 | 0 | 0
40626.5902 | 59.994 | 554.0075 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5903 | 59.991 | 553.3033 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5903 | 59.987 | 553.3033 | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.5903 | 59.987 | 553.3033 | 1 | 0 | 1 | 0 | 0
40626.5903 | 59.986 | 553.9601 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5903 | 59.996 | 553.9601 | 1 | 0 | 1 | 0.0099983 | 0.0099983
40626.5904 | 59.999 | 553.348 | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5904 | 60.001 | 553.348 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5904 | 60.008 | 552.6059 | 1 | 1 | 1 | 0.007 | 0.007
40626.5904 | 60.012 | 552.6059 | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5905 | 60.013 | 552.3778 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5905 | 60.014 | 552.3778 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5905 | 60.013 | 552.1105 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5905 | 60.014 | 552.1105 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5906 | 60.011 | 553.2075 | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.5906 | 60.011 | 553.2075 | 1 | 1 | 1 | 0 | 0
40626.5906 | 60.007 | 553.1398 | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5906 | 60.006 | 553.1398 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5906 | 60.005 | 553.2218 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5907 | 60.004 | 553.2218 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5907 | 60.004 | 553.2479 | 1 | 1 | 1 | 0 | 0
40626.5907 | 60.003 | 553.2479 | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.5907 | 60.005 | 552.1477 | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.5908 | 60.005 | 552.1477 | 1 | 1 | 1 | 0 | 0
40626.5908 | 60.006 | 552.4413 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5908 | 60.005 | 552.4413 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5908 | 60.003 | 552.2262 | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5909 | 60.004 | 552.2262 | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.5909 | 60.002 | 552.241 | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5909 | 60.001 | 552.241 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5909 | 59.998 | 550.9891 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5909 | 59.997 | 550.9891 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.591 | 59.997 | 551.2598 | 1 | 0 | 1 | 0 | 0
40626.591 | 59.995 | 551.2598 | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.591 | 59.994 | 550.8966 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.591 | 59.991 | 550.8966 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5911 | 59.993 | 551.3008 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5911 | 59.993 | 551.3008 | 1 | 0 | 1 | 0 | 0
40626.5911 | 59.99 | 551.201 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5911 | 59.99 | 551.201 | 1 | 0 | 1 | 0 | 0
40626.5912 | 59.988 | 551.0599 | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.5912 | 59.988 | 551.0599 | 1 | 0 | 1 | 0 | 0
40626.5912 | 59.99 | 551.7879 | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.5912 | 59.993 | 551.7879 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5912 | 59.995 | 551.0947 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5913 | 59.997 | 551.0947 | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.5913 | 59.997 | 550.8473 | 1 | 0 | 1 | 0 | 0
40626.5913 | 59.996 | 550.8473 | 1 | 0 | 1 | -0.0010033 | 0.0010033
40626.5913 | 59.993 | 551.1833 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5914 | 59.993 | 551.1833 | 1 | 0 | 1 | 0 | 0
40626.5914 | 59.99 | 551.02 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5914 | 59.994 | 551.02 | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.5914 | 59.992 | 549.6554 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5915 | 59.987 | 549.6554 | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.5915 | 59.984 | 549.2314 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5915 | 59.984 | 549.2314 | 1 | 0 | 1 | 0 | 0
40626.5915 | 59.983 | 549.9525 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5916 | 59.986 | 549.9525 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5916 | 59.986 | 548.9944 | 1 | 0 | 1 | 0 | 0
40626.5916 | 59.986 | 548.9944 | 1 | 0 | 1 | 0 | 0
40626.5916 | 59.986 | 549.8294 | 1 | 0 | 1 | 0 | 0
40626.5916 | 59.988 | 549.8294 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5917 | 59.991 | 549.9199 | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5917 | 59.991 | 549.9199 | 1 | 0 | 1 | 0 | 0
40626.5917 | 59.993 | 549.7203 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5917 | 59.992 | 549.7203 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5918 | 59.99 | 549.6021 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5918 | 59.985 | 549.6021 | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.5918 | 59.984 | 551.3003 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5918 | 59.984 | 551.3003 | 1 | 0 | 1 | 0 | 0
40626.5919 | 59.98 | 551.7938 | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.5919 | 59.978 | 551.7938 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5919 | 59.977 | 550.3602 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5919 | 59.979 | 550.3602 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5919 | 59.976 | 551.4059 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.592 | 59.971 | 551.4059 | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.592 | 59.971 | 550.7222 | 1 | 0 | 1 | 0 | 0
40626.592 | 59.974 | 550.7222 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.592 | 59.98 | 549.7406 | 1 | 0 | 1 | 0.0060005 | 0.0060005
40626.5921 | 59.984 | 549.7406 | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5921 | 59.988 | 550.2887 | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.5921 | 59.992 | 550.2887 | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5921 | 59.997 | 549.5185 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5922 | 60.003 | 549.5185 | 1 | 1 | 1 | 0.0059967 | 0.0059967
40626.5922 | 60.007 | 549.0308 | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5922 | 60.01 | 549.0308 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5922 | 60.013 | 549.8664 | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5922 | 60.015 | 549.8664 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5923 | 60.018 | 550.1417 | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5923 | 60.022 | 550.1417 | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.5923 | 60.026 | 550.1417 | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5923 | 60.025 | 550.1417 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5924 | 60.024 | 548.872 | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.5924 | 60.02 | 548.872 | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.5924 | 60.02 | 549.1459 | 1 | 1 | 1 | 0 | 0
40626.5924 | 60.02 | 549.1459 | 1 | 1 | 1 | 0 | 0
40626.5925 | 60.032 | 549.5798 | 1 | 1 | 1 | 0.012001 | 0.012001
40626.5925 | 60.034 | 549.5798 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5925 | 60.031 | 550.1505 | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5925 | 60.031 | 550.1505 | 1 | 1 | 1 | 0 | 0
40626.5925 | 60.037 | 548.9629 | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.5926 | 60.044 | 548.9629 | 1 | 1 | 1 | 0.007 | 0.007
40626.5926 | 60.039 | 548.272 | 1 | 1 | 1 | -0.0049973 | 0.0049973
40626.5926 | 60.037 | 548.272 | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5926 | 60.038 | 545.4987 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5927 | 60.039 | 545.4987 | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.5927 | 60.039 | 544.7425 | 1 | 1 | 1 | 0 | 0
40626.5927 | 60.044 | 544.7425 | 1 | 1 | 1 | 0.0049973 | 0.0049973
40626.5927 | 60.04 | 544.7425 | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.5928 | 60.036 | 545.0195 | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5928 | 60.034 | 545.4091 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5928 | 60.034 | 545.4091 | 1 | 1 | 1 | 0 | 0
40626.5928 | 60.035 | 545.2927 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5928 | 60.036 | 545.2927 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5929 | 60.035 | 546.0543 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5929 | 60.036 | 546.0543 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5929 | 60.041 | 545.269 | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.5929 | 60.046 | 545.269 | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.593 | 60.043 | 544.9313 | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.593 | 60.037 | 544.9313 | 1 | 1 | 1 | -0.0060005 | 0.0060005
40626.593 | 60.036 | 544.9313 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.593 | 60.034 | 544.0342 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5931 | 60.034 | 542.7912 | 1 | 1 | 1 | 0 | 0
40626.5931 | 60.037 | 542.7912 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5931 | 60.035 | 542.7912 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5931 | 60.031 | 545.318 | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5931 | 60.027 | 545.1019 | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.5932 | 60.026 | 545.1019 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5932 | 60.026 | 546.1512 | 1 | 1 | 1 | 0 | 0
40626.5932 | 60.029 | 546.1512 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5932 | 60.023 | 546.4551 | 1 | 1 | 1 | -0.0060005 | 0.0060005
40626.5933 | 60.023 | 546.4551 | 1 | 1 | 1 | 0 | 0
40626.5933 | 60.023 | 545.0173 | 1 | 1 | 1 | 0 | 0
40626.5933 | 60.024 | 545.0173 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5933 | 60.021 | 545.0173 | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.5934 | 60.022 | 545.3531 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5934 | 60.027 | 544.9564 | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.5934 | 60.028 | 544.9564 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5934 | 60.024 | 544.9564 | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5934 | 60.02 | 544.117 | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.5935 | 60.021 | 544.117 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5935 | 60.023 | 543.8969 | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5935 | 60.025 | 542.3796 | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.5935 | 60.024 | 543.4581 | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.5936 | 60.02 | 543.4581 | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.5936 | 60.016 | 543.4581 | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5936 | 60.013 | 542.5765 | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.5936 | 60.011 | 542.5765 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5937 | 60.006 | 542.5765 | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.5937 | 60.004 | 541.915 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5937 | 60.003 | 540.9343 | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.5937 | 60.003 | 540.9343 | 1 | 1 | 1 | 0 | 0
40626.5938 | 60.005 | 540.9343 | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.5938 | 60.005 | 543.0551 | 1 | 1 | 1 | 0 | 0
40626.5938 | 60.006 | 543.0551 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5938 | 60.006 | 543.0551 | 1 | 1 | 1 | 0 | 0
40626.5938 | 60.014 | 543.0551 | 1 | 1 | 1 | 0.0079994 | 0.0079994
40626.5939 | 60.015 | 544.0527 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5939 | 60.016 | 544.0527 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5939 | 60.02 | 543.6641 | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5939 | 60.02 | 543.6641 | 1 | 1 | 1 | 0 | 0
40626.594 | 60.021 | 544.1694 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.594 | 60.021 | 544.1694 | 1 | 1 | 1 | 0 | 0
40626.594 | 60.019 | 544.341 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.594 | 60.02 | 544.341 | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5941 | 60.025 | 544.7324 | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.5941 | 60.025 | 544.7324 | 1 | 1 | 1 | 0 | 0
40626.5941 | 60.022 | 544.7324 | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5941 | 60.022 | 544.7324 | 1 | 1 | 1 | 0 | 0
40626.5941 | 60.02 | 544.5059 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5942 | 60.019 | 544.5059 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5942 | 60.019 | 545.0428 | 1 | 1 | 1 | 0 | 0
40626.5942 | 60.016 | 545.0428 | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5942 | 60.011 | 545.0089 | 1 | 1 | 1 | -0.0049973 | 0.0049973
40626.5943 | 60.006 | 545.0089 | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.5943 | 60.006 | 545.3657 | 1 | 1 | 1 | 0 | 0
40626.5943 | 59.998 | 545.3657 | 1 | 0 | 1 | -0.0079994 | 0.0079994
40626.5943 | 59.994 | 545.3657 | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.5944 | 59.989 | 545.7728 | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.5944 | 59.986 | 545.7728 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5944 | 59.985 | 545.7592 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5944 | 59.981 | 545.8771 | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.5944 | 59.978 | 545.8771 | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5945 | 59.978 | 545.5687 | 1 | 0 | 1 | 0 | 0
40626.5945 | 59.975 | 545.5687 | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.5945 | 59.975 | 546.2769 | 1 | 0 | 1 | 0 | 0
40626.5945 | 59.964 | 546.2769 | 1 | 0 | 1 | -0.010998 | 0.010998
40626.5946 | 59.964 | 546.4556 | 1 | 0 | 1 | 0 | 0
40626.5946 | 59.964 | 546.4556 | 1 | 0 | 1 | 0 | 0
40626.5946 | 59.96 | 546.4556 | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.5946 | 59.954 | 546.4556 | 1 | 0 | 1 | -0.0060005 | 0.0060005
40626.5947 | 59.95 | 546.5083 | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.5947 | 59.95 | 546.5083 | 1 | 0 | 1 | 0 | 0
40626.5947 | 59.953 | 548.7343 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5947 | 59.952 | 548.7343 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5947 | 59.952 | 548.7343 | 1 | 0 | 1 | 0 | 0
40626.5948 | 59.954 | 550.1754 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5948 | 59.958 | 550.1754 | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5948 | 59.96 | 549.5278 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5948 | 59.96 | 549.5278 | 1 | 0 | 1 | 0 | 0
40626.5949 | 59.958 | 549.5278 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5949 | 59.961 | 549.9443 | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5949 | 59.961 | 549.9443 | 1 | 0 | 1 | 0 | 0
40626.5949 | 59.96 | 548.9269 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.595 | 59.959 | 548.9269 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.595 | 59.961 | 548.9269 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.595 | 59.96 | 550.5129 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.595 | 59.959 | 551.2802 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.595 | 59.96 | 551.2802 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5951 | 59.96 | 551.2802 | 1 | 0 | 1 | 0 | 0
40626.5951 | 59.965 | 551.2802 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5951 | 59.966 | 552.1783 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5951 | 59.965 | 552.4141 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5952 | 59.966 | 553.3627 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5952 | 59.965 | 553.3627 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5952 | 59.959 | 553.3627 | 1 | 0 | 1 | -0.0060005 | 0.0060005
40626.5952 | 59.958 | 552.778 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5953 | 59.96 | 552.2971 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5953 | 59.96 | 552.2971 | 1 | 0 | 1 | 0 | 0
40626.5953 | 59.965 | 552.2971 | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.5953 | 59.964 | 551.7368 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5953 | 59.964 | 552.3671 | 1 | 0 | 1 | 0 | 0
40626.5954 | 59.964 | 553.9274 | 1 | 0 | 1 | 0 | 0
40626.5954 | 59.968 | 553.9274 | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.5954 | 59.968 | 554.131 | 1 | 0 | 1 | 0 | 0
40626.5954 | 59.966 | 554.131 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5955 | 59.966 | 554.1475 | 1 | 0 | 1 | 0 | 0
40626.5955 | 59.97 | 554.1475 | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5955 | 59.972 | 555.1854 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5955 | 59.972 | 555.1854 | 1 | 0 | 1 | 0 | 0
40626.5956 | 59.976 | 554.8472 | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5956 | 59.977 | 554.8472 | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5956 | 59.977 | 555.4637 | 1 | 0 | 1 | 0 | 0
40626.5956 | 59.982 | 555.7798 | 1 | 0 | 1 | 0.0049973 | 0.0049973
40626.5956 | 59.985 | 554.301 | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5957 | 59.983 | 554.1292 | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5957 | 59.981 | 554.1292 | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.5957 | 59.98 | 554.1292 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5957 | 59.979 | 554.2734 | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5958 | 59.981 | 554.2734 | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5958 | 59.981 | 554.0547 | 1 | 0 | 1 | 0 | 0
40626.5958 | 59.984 | 554.0547 | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5958 | 59.988 | 552.8918 | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.5959 | 59.988 | 552.8918 | 1 | 0 | 1 | 0 | 0
40626.5959 | 60.009 | 555.4783 | 1 | 1 | 1 | 0.021 | 0.021
40626.5959 | 60.015 | 555.4783 | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.5959 | 60.021 | 553.1686 | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.5959 | 60.027 | 553.1686 | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.596 | 60.025 | 551.9849 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.596 | 60.025 | 551.9849 | 1 | 1 | 1 | 0 | 0
40626.596 | 60.024 | 552.9873 | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.596 | 60.024 | 552.9873 | 1 | 1 | 1 | 0 | 0
40626.5961 | 60.024 | 553.0009 | 1 | 1 | 1 | 0 | 0
40626.5961 | 60.024 | 553.0009 | 1 | 1 | 1 | 0 | 0
40626.5961 | 60.024 | 552.3838 | 1 | 1 | 1 | 0 | 0
40626.5961 | 60.023 | 552.3838 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5962 | 60.027 | 553.2295 | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5962 | 60.027 | 553.2295 | 1 | 1 | 1 | 0 | 0
40626.5962 | 60.027 | 552.9197 | 1 | 1 | 1 | 0 | 0
40626.5962 | 60.027 | 552.9197 | 1 | 1 | 1 | 0 | 0
40626.5963 | 60.024 | 552.3134 | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5963 | 60.024 | 552.3134 | 1 | 1 | 1 | 0 | 0
40626.5963 | 60.023 | 552.5338 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5963 | 60.023 | 552.5338 | 1 | 1 | 1 | 0 | 0
40626.5963 | 60.021 | 552.051 | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5964 | 60.017 | 552.051 | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5964 | 60.017 | 552.1459 | 1 | 1 | 1 | 0 | 0
40626.5964 | 60.021 | 552.1459 | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5964 | 60.025 | 550.653 | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5965 | 60.028 | 549.58 | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5965 | 60.027 | 549.58 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5965 | 60.02 | 549.58 | 1 | 1 | 1 | -0.007 | 0.007
40626.5965 | 60.019 | 551.2336 | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5966 | 60.019 |  | 1 | 1 | 1 | 0 | 0
40626.5966 | 60.019 |  | 1 | 1 | 1 | 0 | 0
40626.5966 | 60.02 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5966 | 60.02 |  | 1 | 1 | 1 | 0 | 0
40626.5966 | 60.019 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5967 | 60.015 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5967 | 60.015 |  | 1 | 1 | 1 | 0 | 0
40626.5967 | 60.013 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5967 | 60.011 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5968 | 59.999 |  | 1 | 0 | 1 | -0.012001 | 0.012001
40626.5968 | 59.999 |  | 1 | 0 | 1 | 0 | 0
40626.5968 | 59.995 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.5968 | 59.99 |  | 1 | 0 | 1 | -0.0049973 | 0.0049973
40626.5969 | 59.987 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.5969 | 59.987 |  | 1 | 0 | 1 | 0 | 0
40626.5969 | 59.987 |  | 1 | 0 | 1 | 0 | 0
40626.5969 | 59.987 |  | 1 | 0 | 1 | 0 | 0
40626.5969 | 59.987 |  | 1 | 0 | 1 | 0 | 0
40626.597 | 59.987 |  | 1 | 0 | 1 | 0 | 0
40626.597 | 59.987 |  | 1 | 0 | 1 | 0 | 0
40626.597 | 59.986 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.597 | 59.984 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5971 | 59.989 |  | 1 | 0 | 1 | 0.0049973 | 0.0049973
40626.5971 | 59.989 |  | 1 | 0 | 1 | 0 | 0
40626.5971 | 59.989 |  | 1 | 0 | 1 | 0 | 0
40626.5971 | 59.99 |  | 1 | 0 | 1 | 0.0010033 | 0.0010033
40626.5972 | 59.99 |  | 1 | 0 | 1 | 0 | 0
40626.5972 | 59.991 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5972 | 59.988 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.5972 | 59.976 |  | 1 | 0 | 1 | -0.011997 | 0.011997
40626.5972 | 59.976 |  | 1 | 0 | 1 | 0 | 0
40626.5973 | 59.97 |  | 1 | 0 | 1 | -0.0060005 | 0.0060005
40626.5973 | 59.972 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5973 | 59.972 |  | 1 | 0 | 1 | 0 | 0
40626.5973 | 59.975 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5974 | 59.979 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5974 | 59.98 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5974 | 59.978 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5974 | 59.974 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.5975 | 59.972 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5975 | 59.971 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5975 | 59.973 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5975 | 59.976 |  | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5975 | 59.977 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5976 | 59.977 |  | 1 | 0 | 1 | 0 | 0
40626.5976 | 59.979 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5976 | 59.981 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5976 | 59.984 |  | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5977 | 59.986 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5977 | 59.988 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.5977 | 59.991 |  | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.5977 | 59.992 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5978 | 59.991 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5978 | 59.991 |  | 1 | 0 | 1 | 0 | 0
40626.5978 | 59.994 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.5978 | 59.998 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.5978 | 60.002 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.5979 | 60.005 |  | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5979 | 60.009 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.5979 | 60.01 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5979 | 60.011 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.598 | 60.01 |  | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.598 | 60.009 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.598 | 60.006 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.598 | 60.004 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5981 | 60.001 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5981 | 60.003 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5981 | 60.002 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5981 | 60.004 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.5981 | 60.009 |  | 1 | 1 | 1 | 0.0049973 | 0.0049973
40626.5982 | 60.014 |  | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.5982 | 60.018 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5982 | 60.022 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.5982 | 60.022 |  | 1 | 1 | 1 | 0 | 0
40626.5983 | 60.021 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5983 | 60.021 |  | 1 | 1 | 1 | 0 | 0
40626.5983 | 60.029 |  | 1 | 1 | 1 | 0.0079994 | 0.0079994
40626.5983 | 60.028 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5984 | 60.031 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.5984 | 60.034 |  | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5984 | 60.031 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5984 | 60.029 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5984 | 60.03 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5985 | 60.031 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5985 | 60.032 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.5985 | 60.03 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5985 | 60.029 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5986 | 60.033 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.5986 | 60.032 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5986 | 60.028 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5986 | 60.027 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5987 | 60.028 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5987 | 60.03 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5987 | 60.036 |  | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.5987 | 60.033 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.5987 | 60.031 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.5988 | 60.031 |  | 1 | 1 | 1 | 0 | 0
40626.5988 | 60.034 |  | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5988 | 60.034 |  | 1 | 1 | 1 | 0 | 0
40626.5988 | 60.032 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5989 | 60.031 |  | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.5989 | 60.031 |  | 1 | 1 | 1 | 0 | 0
40626.5989 | 60.028 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.5989 | 60.026 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.599 | 60.022 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.599 | 60.022 |  | 1 | 1 | 1 | 0 | 0
40626.599 | 60.021 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.599 | 60.022 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5991 | 60.022 |  | 1 | 1 | 1 | 0 | 0
40626.5991 | 60.02 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5991 | 60.019 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5991 | 60.02 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5991 | 60.022 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5992 | 60.023 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.5992 | 60.022 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5992 | 60.02 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5992 | 60.017 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.5993 | 60.015 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.5993 | 60.018 |  | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5993 | 60.02 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.5993 | 60.02 |  | 1 | 1 | 1 | 0 | 0
40626.5994 | 60.024 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.5994 | 60.027 |  | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.5994 | 60.027 |  | 1 | 1 | 1 | 0 | 0
40626.5994 | 60.023 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5994 | 60.023 |  | 1 | 1 | 1 | 0 | 0
40626.5995 | 60.018 |  | 1 | 1 | 1 | -0.0049973 | 0.0049973
40626.5995 | 60.012 |  | 1 | 1 | 1 | -0.0060005 | 0.0060005
40626.5995 | 60.006 |  | 1 | 1 | 1 | -0.0060005 | 0.0060005
40626.5995 | 60.006 |  | 1 | 1 | 1 | 0 | 0
40626.5996 | 60.002 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.5996 | 60.002 |  | 1 | 1 | 1 | 0 | 0
40626.5996 | 60.001 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.5996 | 59.999 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5997 | 59.999 |  | 1 | 0 | 1 | 0 | 0
40626.5997 | 59.998 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5997 | 59.995 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.5997 | 59.992 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.5997 | 59.988 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.5998 | 59.986 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.5998 | 59.985 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5998 | 59.984 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5998 | 59.985 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.5999 | 59.984 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5999 | 59.984 |  | 1 | 0 | 1 | 0 | 0
40626.5999 | 59.983 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.5999 | 59.981 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6 | 59.979 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6 | 59.98 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6 | 59.977 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6 | 59.977 |  | 1 | 0 | 1 | 0 | 0
40626.6 | 59.977 |  | 1 | 0 | 1 | 0 | 0
40626.6001 | 59.976 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6001 | 59.977 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6001 | 59.977 |  | 1 | 0 | 1 | 0 | 0
40626.6001 | 59.978 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6002 | 59.981 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6002 | 59.98 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6002 | 59.984 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6002 | 59.985 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6003 | 59.985 |  | 1 | 0 | 1 | 0 | 0
40626.6003 | 59.988 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6003 | 59.986 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6003 | 59.988 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6003 | 59.988 |  | 1 | 0 | 1 | 0 | 0
40626.6004 | 59.986 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6004 | 59.988 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6004 | 59.987 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6004 | 59.984 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6005 | 59.983 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6005 | 59.983 |  | 1 | 0 | 1 | 0 | 0
40626.6005 | 59.984 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6005 | 59.985 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6006 | 59.983 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6006 | 59.983 |  | 1 | 0 | 1 | 0 | 0
40626.6006 | 59.986 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6006 | 59.988 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6006 | 59.993 |  | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.6007 | 59.997 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6007 | 59.998 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6007 | 59.998 |  | 1 | 0 | 1 | 0 | 0
40626.6007 | 60.002 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.6008 | 60.004 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6008 | 60.005 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6008 | 60.003 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6008 | 60.003 |  | 1 | 1 | 1 | 0 | 0
40626.6009 | 60.005 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6009 | 60.01 |  | 1 | 1 | 1 | 0.0049973 | 0.0049973
40626.6009 | 60.015 |  | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.6009 | 60.016 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6009 | 60.022 |  | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.601 | 60.023 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.601 | 60.024 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.601 | 60.024 |  | 1 | 1 | 1 | 0 | 0
40626.601 | 60.023 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6011 | 60.024 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6011 | 60.025 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6011 | 60.029 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.6011 | 60.029 |  | 1 | 1 | 1 | 0 | 0
40626.6012 | 60.028 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6012 | 60.025 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6012 | 60.027 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6012 | 60.024 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6012 | 60.027 |  | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.6013 | 60.024 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6013 | 60.022 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6013 | 60.02 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6013 | 60.016 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.6014 | 60.014 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6014 | 60.016 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6014 | 60.017 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6014 | 60.02 |  | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.6015 | 60.025 |  | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.6015 | 60.028 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6015 | 60.03 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6015 | 60.032 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6016 | 60.036 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.6016 | 60.036 |  | 1 | 1 | 1 | 0 | 0
40626.6016 | 60.031 |  | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.6016 | 60.027 |  | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.6016 | 60.025 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6017 | 60.031 |  | 1 | 1 | 1 | 0.0059967 | 0.0059967
40626.6017 | 60.027 |  | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.6017 | 60.029 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6017 | 60.03 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6018 | 60.03 |  | 1 | 1 | 1 | 0 | 0
40626.6018 | 60.034 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6018 | 60.035 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6018 | 60.032 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6019 | 60.03 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6019 | 60.029 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6019 | 60.026 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6019 | 60.028 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6019 | 60.027 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.602 | 60.027 |  | 1 | 1 | 1 | 0 | 0
40626.602 | 60.03 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.602 | 60.031 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.602 | 60.032 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6021 | 60.034 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6021 | 60.032 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6021 | 60.03 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6021 | 60.03 |  | 1 | 1 | 1 | 0 | 0
40626.6022 | 60.03 |  | 1 | 1 | 1 | 0 | 0
40626.6022 | 60.031 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6022 | 60.029 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6022 | 60.035 |  | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.6022 | 60.039 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6023 | 60.036 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6023 | 60.035 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6023 | 60.033 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6023 | 60.031 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6024 | 60.032 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6024 | 60.031 |  | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.6024 | 60.036 |  | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.6024 | 60.035 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6025 | 60.037 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6025 | 60.036 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6025 | 60.036 |  | 1 | 1 | 1 | 0 | 0
40626.6025 | 60.035 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6025 | 60.036 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6026 | 60.036 |  | 1 | 1 | 1 | 0 | 0
40626.6026 | 60.038 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6026 | 60.039 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6026 | 60.039 |  | 1 | 1 | 1 | 0 | 0
40626.6027 | 60.038 |  | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.6027 | 60.039 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6027 | 60.041 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6027 | 60.04 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6028 | 60.037 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6028 | 60.035 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6028 | 60.033 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6028 | 60.032 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6028 | 60.03 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6029 | 60.033 |  | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.6029 | 60.035 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6029 | 60.034 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6029 | 60.038 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.603 | 60.035 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.603 | 60.034 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.603 | 60.032 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.603 | 60.029 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6031 | 60.035 |  | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.6031 | 60.037 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6031 | 60.039 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6031 | 60.037 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6031 | 60.035 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6032 | 60.036 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6032 | 60.035 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6032 | 60.032 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6032 | 60.03 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6033 | 60.027 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6033 | 60.027 |  | 1 | 1 | 1 | 0 | 0
40626.6033 | 60.027 |  | 1 | 1 | 1 | 0 | 0
40626.6033 | 60.037 |  | 1 | 1 | 1 | 0.0099983 | 0.0099983
40626.6034 | 60.043 |  | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.6034 | 60.04 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6034 | 60.044 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.6034 | 60.046 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6034 | 60.043 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6035 | 60.04 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6035 | 60.038 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6035 | 60.043 |  | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.6035 | 60.043 |  | 1 | 1 | 1 | 0 | 0
40626.6036 | 60.041 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6036 | 60.041 |  | 1 | 1 | 1 | 0 | 0
40626.6036 | 60.039 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6036 | 60.04 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6037 | 60.043 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6037 | 60.045 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6037 | 60.04 |  | 1 | 1 | 1 | -0.0049973 | 0.0049973
40626.6037 | 60.039 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6038 | 60.039 |  | 1 | 1 | 1 | 0 | 0
40626.6038 | 60.041 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6038 | 60.043 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6038 | 60.044 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6038 | 60.041 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6039 | 60.04 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6039 | 60.04 |  | 1 | 1 | 1 | 0 | 0
40626.6039 | 60.04 |  | 1 | 1 | 1 | 0 | 0
40626.6039 | 60.036 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.604 | 60.038 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.604 | 60.033 |  | 1 | 1 | 1 | -0.0049973 | 0.0049973
40626.604 | 60.029 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.604 | 60.03 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6041 | 60.028 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6041 | 60.028 |  | 1 | 1 | 1 | 0 | 0
40626.6041 | 60.032 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6041 | 60.035 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6041 | 60.038 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6042 | 60.036 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6042 | 60.036 |  | 1 | 1 | 1 | 0 | 0
40626.6042 | 60.034 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6042 | 60.034 |  | 1 | 1 | 1 | 0 | 0
40626.6043 | 60.029 |  | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.6043 | 60.029 |  | 1 | 1 | 1 | 0 | 0
40626.6043 | 60.029 |  | 1 | 1 | 1 | 0 | 0
40626.6043 | 60.028 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6044 | 60.029 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6044 | 60.029 |  | 1 | 1 | 1 | 0 | 0
40626.6044 | 60.031 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6044 | 60.031 |  | 1 | 1 | 1 | 0 | 0
40626.6044 | 60.031 |  | 1 | 1 | 1 | 0 | 0
40626.6045 | 60.031 |  | 1 | 1 | 1 | 0 | 0
40626.6045 | 60.027 |  | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.6045 | 60.028 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6045 | 60.025 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6046 | 60.026 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6046 | 60.026 |  | 1 | 1 | 1 | 0 | 0
40626.6046 | 60.03 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.6046 | 60.034 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6047 | 60.034 |  | 1 | 1 | 1 | 0 | 0
40626.6047 | 60.03 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.6047 | 60.028 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6047 | 60.028 |  | 1 | 1 | 1 | 0 | 0
40626.6047 | 60.028 |  | 1 | 1 | 1 | 0 | 0
40626.6048 | 60.033 |  | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.6048 | 60.033 |  | 1 | 1 | 1 | 0 | 0
40626.6048 | 60.037 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.6048 | 60.037 |  | 1 | 1 | 1 | 0 | 0
40626.6049 | 60.036 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6049 | 60.035 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6049 | 60.036 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6049 | 60.036 |  | 1 | 1 | 1 | 0 | 0
40626.605 | 60.038 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.605 | 60.038 |  | 1 | 1 | 1 | 0 | 0
40626.605 | 60.038 |  | 1 | 1 | 1 | 0 | 0
40626.605 | 60.038 |  | 1 | 1 | 1 | 0 | 0
40626.605 | 60.046 |  | 1 | 1 | 1 | 0.0080032 | 0.0080032
40626.6051 | 60.048 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6051 | 60.048 |  | 1 | 1 | 1 | 0 | 0
40626.6051 | 60.042 |  | 1 | 1 | 1 | -0.0060005 | 0.0060005
40626.6051 | 60.041 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6052 | 60.043 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6052 | 60.04 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6052 | 60.04 |  | 1 | 1 | 1 | 0 | 0
40626.6052 | 60.036 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.6053 | 60.033 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6053 | 60.032 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6053 | 60.031 |  | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.6053 | 60.028 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6053 | 60.025 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6054 | 60.021 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.6054 | 60.02 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6054 | 60.022 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6054 | 60.026 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6055 | 60.027 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6055 | 60.028 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6055 | 60.028 |  | 1 | 1 | 1 | 0 | 0
40626.6055 | 60.026 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6056 | 60.024 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6056 | 60.025 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6056 | 60.026 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6056 | 60.029 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6056 | 60.028 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6057 | 60.027 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6057 | 60.028 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6057 | 60.028 |  | 1 | 1 | 1 | 0 | 0
40626.6057 | 60.029 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6058 | 60.028 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6058 | 60.026 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6058 | 60.025 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6058 | 60.03 |  | 1 | 1 | 1 | 0.0049973 | 0.0049973
40626.6059 | 60.032 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6059 | 60.03 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6059 | 60.03 |  | 1 | 1 | 1 | 0 | 0
40626.6059 | 60.03 |  | 1 | 1 | 1 | 0 | 0
40626.6059 | 60.03 |  | 1 | 1 | 1 | 0 | 0
40626.606 | 60.031 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.606 | 60.035 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.606 | 60.037 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.606 | 60.036 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6061 | 60.036 |  | 1 | 1 | 1 | 0 | 0
40626.6061 | 60.033 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6061 | 60.028 |  | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.6061 | 60.027 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6062 | 60.032 |  | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.6062 | 60.03 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6062 | 60.029 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6062 | 60.027 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6062 | 60.026 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6063 | 60.026 |  | 1 | 1 | 1 | 0 | 0
40626.6063 | 60.026 |  | 1 | 1 | 1 | 0 | 0
40626.6063 | 60.023 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6063 | 60.024 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6064 | 60.02 |  | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.6064 | 60.018 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6064 | 60.016 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6064 | 60.026 |  | 1 | 1 | 1 | 0.010002 | 0.010002
40626.6065 | 60.035 |  | 1 | 1 | 1 | 0.0089989 | 0.0089989
40626.6065 | 60.038 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6065 | 60.036 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6065 | 60.037 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6066 | 60.038 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6066 | 60.037 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6066 | 60.037 |  | 1 | 1 | 1 | 0 | 0
40626.6066 | 60.036 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6066 | 60.036 |  | 1 | 1 | 1 | 0 | 0
40626.6067 | 60.036 |  | 1 | 1 | 1 | 0 | 0
40626.6067 | 60.034 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6067 | 60.037 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6067 | 60.038 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6068 | 60.037 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6068 | 60.038 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6068 | 60.04 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6068 | 60.038 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6069 | 60.031 |  | 1 | 1 | 1 | -0.007 | 0.007
40626.6069 | 60.027 |  | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.6069 | 60.023 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.6069 | 60.02 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6069 | 60.016 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.607 | 60.013 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.607 | 60.009 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.607 | 60.004 |  | 1 | 1 | 1 | -0.0049973 | 0.0049973
40626.607 | 60 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.6071 | 59.995 |  | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.6071 | 59.991 |  | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.6071 | 59.991 |  | 1 | 0 | 1 | 0 | 0
40626.6071 | 59.991 |  | 1 | 0 | 1 | 0 | 0
40626.6072 | 59.99 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6072 | 59.989 |  | 1 | 0 | 1 | -0.0010033 | 0.0010033
40626.6072 | 59.986 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6072 | 59.984 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6072 | 59.982 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6073 | 59.986 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6073 | 59.989 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6073 | 59.986 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6073 | 59.986 |  | 1 | 0 | 1 | 0 | 0
40626.6074 | 59.987 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6074 | 59.988 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6074 | 59.988 |  | 1 | 0 | 1 | 0 | 0
40626.6074 | 59.986 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6075 | 59.983 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6075 | 59.981 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6075 | 59.982 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6075 | 59.981 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6075 | 59.981 |  | 1 | 0 | 1 | 0 | 0
40626.6076 | 59.977 |  | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.6076 | 59.974 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.6076 | 59.974 |  | 1 | 0 | 1 | 0 | 0
40626.6076 | 59.979 |  | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.6077 | 59.978 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6077 | 59.974 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.6077 | 59.974 |  | 1 | 0 | 1 | 0 | 0
40626.6077 | 59.976 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6078 | 59.978 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6078 | 59.981 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6078 | 59.981 |  | 1 | 0 | 1 | 0 | 0
40626.6078 | 59.985 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6078 | 59.988 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6079 | 59.989 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6079 | 59.996 |  | 1 | 0 | 1 | 0.007 | 0.007
40626.6079 | 59.998 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6079 | 60.003 |  | 1 | 1 | 1 | 0.0049973 | 0.0049973
40626.608 | 60.012 |  | 1 | 1 | 1 | 0.0090027 | 0.0090027
40626.608 | 60.015 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.608 | 60.019 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.608 | 60.02 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6081 | 60.02 |  | 1 | 1 | 1 | 0 | 0
40626.6081 | 60.02 |  | 1 | 1 | 1 | 0 | 0
40626.6081 | 60.021 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6081 | 60.024 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6081 | 60.027 |  | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.6082 | 60.028 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6082 | 60.026 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6082 | 60.026 |  | 1 | 1 | 1 | 0 | 0
40626.6082 | 60.028 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6083 | 60.029 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6083 | 60.03 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6083 | 60.031 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6083 | 60.031 |  | 1 | 1 | 1 | 0 | 0
40626.6084 | 60.031 |  | 1 | 1 | 1 | 0 | 0
40626.6084 | 60.03 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6084 | 60.027 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6084 | 60.03 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6084 | 60.024 |  | 1 | 1 | 1 | -0.0060005 | 0.0060005
40626.6085 | 60.019 |  | 1 | 1 | 1 | -0.0049973 | 0.0049973
40626.6085 | 60.018 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6085 | 60.018 |  | 1 | 1 | 1 | 0 | 0
40626.6085 | 60.021 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6086 | 60.024 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6086 | 60.029 |  | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.6086 | 60.028 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6086 | 60.025 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6087 | 60.024 |  | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.6087 | 60.02 |  | 1 | 1 | 1 | -0.0039978 | 0.0039978
40626.6087 | 60.017 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6087 | 60.017 |  | 1 | 1 | 1 | 0 | 0
40626.6087 | 60.018 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6088 | 60.018 |  | 1 | 1 | 1 | 0 | 0
40626.6088 | 60.022 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.6088 | 60.026 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6088 | 60.025 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6089 | 60.022 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6089 | 60.022 |  | 1 | 1 | 1 | 0 | 0
40626.6089 | 60.021 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6089 | 60.02 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.609 | 60.019 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.609 | 60.015 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.609 | 60.012 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.609 | 60.007 |  | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.6091 | 60 |  | 1 | 0 | 1 | -0.007 | 0.007
40626.6091 | 59.995 |  | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.6091 | 59.989 |  | 1 | 0 | 1 | -0.0060005 | 0.0060005
40626.6091 | 59.986 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6091 | 59.983 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6092 | 59.979 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.6092 | 59.974 |  | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.6092 | 59.971 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6092 | 59.972 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6093 | 59.978 |  | 1 | 0 | 1 | 0.0060005 | 0.0060005
40626.6093 | 59.981 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6093 | 59.982 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6093 | 59.982 |  | 1 | 0 | 1 | 0 | 0
40626.6094 | 59.983 |  | 1 | 0 | 1 | 0.0010033 | 0.0010033
40626.6094 | 59.983 |  | 1 | 0 | 1 | 0 | 0
40626.6094 | 59.983 |  | 1 | 0 | 1 | 0 | 0
40626.6094 | 59.98 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.6094 | 59.972 |  | 1 | 0 | 1 | -0.0079994 | 0.0079994
40626.6095 | 59.971 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6095 | 59.973 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6095 | 59.976 |  | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.6095 | 59.97 |  | 1 | 0 | 1 | -0.0060005 | 0.0060005
40626.6096 | 59.969 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6096 | 59.97 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6096 | 59.967 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.6096 | 59.964 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6097 | 59.967 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6097 | 59.963 |  | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.6097 | 59.964 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6097 | 59.968 |  | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.6097 | 59.968 |  | 1 | 0 | 1 | 0 | 0
40626.6098 | 59.968 |  | 1 | 0 | 1 | 0 | 0
40626.6098 | 59.968 |  | 1 | 0 | 1 | 0 | 0
40626.6098 | 59.969 |  | 1 | 0 | 1 | 0.0010033 | 0.0010033
40626.6098 | 59.97 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6099 | 59.972 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6099 | 59.972 |  | 1 | 0 | 1 | 0 | 0
40626.6099 | 59.97 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6099 | 59.968 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.61 | 59.976 |  | 1 | 0 | 1 | 0.0080032 | 0.0080032
40626.61 | 59.99 |  | 1 | 0 | 1 | 0.014 | 0.014
40626.61 | 59.99 |  | 1 | 0 | 1 | 0 | 0
40626.61 | 59.995 |  | 1 | 0 | 1 | 0.0049973 | 0.0049973
40626.61 | 59.994 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6101 | 59.994 |  | 1 | 0 | 1 | 0 | 0
40626.6101 | 60.001 |  | 1 | 1 | 1 | 0.007 | 0.007
40626.6101 | 60.001 |  | 1 | 1 | 1 | 0 | 0
40626.6101 | 60 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6102 | 60.001 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6102 | 60.003 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6102 | 60.003 |  | 1 | 1 | 1 | 0 | 0
40626.6102 | 60.004 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6103 | 60.005 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6103 | 60.008 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6103 | 60.011 |  | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.6103 | 60.009 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6103 | 60.008 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6104 | 60.008 |  | 1 | 1 | 1 | 0 | 0
40626.6104 | 60.009 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6104 | 60.01 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6104 | 60.012 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6105 | 60.012 |  | 1 | 1 | 1 | 0 | 0
40626.6105 | 60.014 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6105 | 60.014 |  | 1 | 1 | 1 | 0 | 0
40626.6105 | 60.017 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6106 | 60.017 |  | 1 | 1 | 1 | 0 | 0
40626.6106 | 60.019 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6106 | 60.018 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6106 | 60.018 |  | 1 | 1 | 1 | 0 | 0
40626.6106 | 60.017 |  | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.6107 | 60.017 |  | 1 | 1 | 1 | 0 | 0
40626.6107 | 60.018 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6107 | 60.018 |  | 1 | 1 | 1 | 0 | 0
40626.6107 | 60.022 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.6108 | 60.026 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6108 | 60.029 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6108 | 60.027 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6108 | 60.025 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6109 | 60.023 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6109 | 60.017 |  | 1 | 1 | 1 | -0.0060005 | 0.0060005
40626.6109 | 60.017 |  | 1 | 1 | 1 | 0 | 0
40626.6109 | 60.018 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6109 | 60.015 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.611 | 60.014 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.611 | 60.015 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.611 | 60.017 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.611 | 60.015 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6111 | 60.013 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6111 | 60.012 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6111 | 60.01 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6111 | 60.008 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6112 | 60.006 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6112 | 60.006 |  | 1 | 1 | 1 | 0 | 0
40626.6112 | 60.009 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6112 | 60.011 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6113 | 60.007 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.6113 | 59.997 |  | 1 | 0 | 1 | -0.0099983 | 0.0099983
40626.6113 | 59.989 |  | 1 | 0 | 1 | -0.0080032 | 0.0080032
40626.6113 | 59.988 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6113 | 59.984 |  | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.6114 | 59.984 |  | 1 | 0 | 1 | 0 | 0
40626.6114 | 59.985 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6114 | 59.989 |  | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.6114 | 59.992 |  | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.6115 | 59.992 |  | 1 | 0 | 1 | 0 | 0
40626.6115 | 59.993 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6115 | 59.993 |  | 1 | 0 | 1 | 0 | 0
40626.6115 | 59.996 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6116 | 59.997 |  | 1 | 0 | 1 | 0.0010033 | 0.0010033
40626.6116 | 59.999 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6116 | 59.997 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6116 | 59.996 |  | 1 | 0 | 1 | -0.0010033 | 0.0010033
40626.6116 | 59.993 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6117 | 59.983 |  | 1 | 0 | 1 | -0.0099983 | 0.0099983
40626.6117 | 59.969 |  | 1 | 0 | 1 | -0.014 | 0.014
40626.6117 | 59.967 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6117 | 59.959 |  | 1 | 0 | 1 | -0.0079994 | 0.0079994
40626.6118 | 59.954 |  | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.6118 | 59.943 |  | 1 | 0 | 1 | -0.010998 | 0.010998
40626.6118 | 59.937 |  | 1 | 0 | 1 | -0.0060005 | 0.0060005
40626.6118 | 59.936 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6119 | 59.939 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6119 | 59.946 |  | 1 | 0 | 1 | 0.007 | 0.007
40626.6119 | 59.956 |  | 1 | 0 | 1 | 0.010002 | 0.010002
40626.6119 | 59.959 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6119 | 59.963 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.612 | 59.956 |  | 1 | 0 | 1 | -0.007 | 0.007
40626.612 | 59.956 |  | 1 | 0 | 1 | 0 | 0
40626.612 | 59.96 |  | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.612 | 59.963 |  | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.6121 | 59.962 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6121 | 59.958 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.6121 | 59.958 |  | 1 | 0 | 1 | 0 | 0
40626.6121 | 59.96 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6122 | 59.96 |  | 1 | 0 | 1 | 0 | 0
40626.6122 | 59.958 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6122 | 59.957 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6122 | 59.961 |  | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.6122 | 59.96 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6123 | 59.959 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6123 | 59.955 |  | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.6123 | 59.954 |  | 1 | 0 | 1 | -0.0010033 | 0.0010033
40626.6123 | 59.951 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6124 | 59.954 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6124 | 59.951 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6124 | 59.951 |  | 1 | 0 | 1 | 0 | 0
40626.6124 | 59.951 |  | 1 | 0 | 1 | 0 | 0
40626.6125 | 59.953 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6125 | 59.958 |  | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.6125 | 59.955 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6125 | 59.956 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6125 | 59.955 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6126 | 59.955 |  | 1 | 0 | 1 | 0 | 0
40626.6126 | 59.956 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6126 | 59.955 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6126 | 59.951 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.6127 | 59.949 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6127 | 59.947 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6127 | 59.951 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6127 | 59.95 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6128 | 59.95 |  | 1 | 0 | 1 | 0 | 0
40626.6128 | 59.95 |  | 1 | 0 | 1 | 0 | 0
40626.6128 | 59.948 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6128 | 59.947 |  | 1 | 0 | 1 | -0.0010033 | 0.0010033
40626.6128 | 59.949 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6129 | 59.948 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6129 | 59.948 |  | 1 | 0 | 1 | 0 | 0
40626.6129 | 59.948 |  | 1 | 0 | 1 | 0 | 0
40626.6129 | 59.951 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.613 | 59.952 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.613 | 59.952 |  | 1 | 0 | 1 | 0 | 0
40626.613 | 59.951 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.613 | 59.949 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6131 | 59.949 |  | 1 | 0 | 1 | 0 | 0
40626.6131 | 59.952 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6131 | 59.957 |  | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.6131 | 59.959 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6131 | 59.961 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6132 | 59.96 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6132 | 59.966 |  | 1 | 0 | 1 | 0.0060005 | 0.0060005
40626.6132 | 59.963 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6132 | 59.963 |  | 1 | 0 | 1 | 0 | 0
40626.6133 | 59.964 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6133 | 59.964 |  | 1 | 0 | 1 | 0 | 0
40626.6133 | 59.965 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6133 | 59.967 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6134 | 59.967 |  | 1 | 0 | 1 | 0 | 0
40626.6134 | 59.966 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6134 | 59.966 |  | 1 | 0 | 1 | 0 | 0
40626.6134 | 59.963 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6134 | 59.964 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6135 | 59.967 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6135 | 59.971 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6135 | 59.975 |  | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.6135 | 59.979 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6136 | 59.979 |  | 1 | 0 | 1 | 0 | 0
40626.6136 | 59.977 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6136 | 59.974 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.6136 | 59.973 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6137 | 59.973 |  | 1 | 0 | 1 | 0 | 0
40626.6137 | 59.976 |  | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.6137 | 59.977 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6137 | 59.976 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6137 | 59.973 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.6138 | 59.974 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6138 | 59.976 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6138 | 59.974 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6138 | 59.972 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6139 | 59.97 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6139 | 59.969 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6139 | 59.968 |  | 1 | 0 | 1 | -0.0010033 | 0.0010033
40626.6139 | 59.968 |  | 1 | 0 | 1 | 0 | 0
40626.614 | 59.968 |  | 1 | 0 | 1 | 0 | 0
40626.614 | 59.967 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.614 | 59.967 |  | 1 | 0 | 1 | 0 | 0
40626.614 | 59.966 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6141 | 59.969 |  | 1 | 0 | 1 | 0.0030022 | 0.0030022
40626.6141 | 59.975 |  | 1 | 0 | 1 | 0.0059967 | 0.0059967
40626.6141 | 59.979 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6141 | 59.978 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6141 | 59.973 |  | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.6142 | 59.973 |  | 1 | 0 | 1 | 0 | 0
40626.6142 | 59.975 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6142 | 59.973 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6142 | 59.972 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6143 | 59.973 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6143 | 59.973 |  | 1 | 0 | 1 | 0 | 0
40626.6143 | 59.97 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6143 | 59.969 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6144 | 59.965 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.6144 | 59.967 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6144 | 59.961 |  | 1 | 0 | 1 | -0.0060005 | 0.0060005
40626.6144 | 59.957 |  | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.6144 | 59.955 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6145 | 59.958 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6145 | 59.959 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6145 | 59.964 |  | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.6145 | 59.966 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6146 | 59.967 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6146 | 59.967 |  | 1 | 0 | 1 | 0 | 0
40626.6146 | 59.967 |  | 1 | 0 | 1 | 0 | 0
40626.6146 | 59.969 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6147 | 59.966 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.6147 | 59.967 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6147 | 59.967 |  | 1 | 0 | 1 | 0 | 0
40626.6147 | 59.969 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6147 | 59.972 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6148 | 59.972 |  | 1 | 0 | 1 | 0 | 0
40626.6148 | 59.972 |  | 1 | 0 | 1 | 0 | 0
40626.6148 | 59.972 |  | 1 | 0 | 1 | 0 | 0
40626.6148 | 59.971 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6149 | 59.971 |  | 1 | 0 | 1 | 0 | 0
40626.6149 | 59.97 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6149 | 59.973 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6149 | 59.973 |  | 1 | 0 | 1 | 0 | 0
40626.615 | 59.971 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.615 | 59.967 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.615 | 59.967 |  | 1 | 0 | 1 | 0 | 0
40626.615 | 59.965 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.615 | 59.963 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6151 | 59.967 |  | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.6151 | 59.967 |  | 1 | 0 | 1 | 0 | 0
40626.6151 | 59.966 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6151 | 59.974 |  | 1 | 0 | 1 | 0.0079994 | 0.0079994
40626.6152 | 59.981 |  | 1 | 0 | 1 | 0.007 | 0.007
40626.6152 | 59.983 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6152 | 59.986 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6152 | 59.988 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6153 | 59.985 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6153 | 59.984 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6153 | 59.984 |  | 1 | 0 | 1 | 0 | 0
40626.6153 | 59.987 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6153 | 59.987 |  | 1 | 0 | 1 | 0 | 0
40626.6154 | 59.987 |  | 1 | 0 | 1 | 0 | 0
40626.6154 | 59.987 |  | 1 | 0 | 1 | 0 | 0
40626.6154 | 59.989 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6154 | 59.991 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6155 | 59.993 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6155 | 59.995 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6155 | 59.995 |  | 1 | 0 | 1 | 0 | 0
40626.6155 | 59.993 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6156 | 59.989 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.6156 | 59.984 |  | 1 | 0 | 1 | -0.0049973 | 0.0049973
40626.6156 | 59.982 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6156 | 59.98 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6156 | 59.975 |  | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.6157 | 59.973 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6157 | 59.973 |  | 1 | 0 | 1 | 0 | 0
40626.6157 | 59.969 |  | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.6157 | 59.971 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6158 | 59.965 |  | 1 | 0 | 1 | -0.0060005 | 0.0060005
40626.6158 | 59.963 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6158 | 59.963 |  | 1 | 0 | 1 | 0 | 0
40626.6158 | 59.961 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6159 | 59.961 |  | 1 | 0 | 1 | 0 | 0
40626.6159 | 59.965 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6159 | 59.967 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6159 | 59.969 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6159 | 59.973 |  | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.616 | 59.979 |  | 1 | 0 | 1 | 0.0060005 | 0.0060005
40626.616 | 59.981 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.616 | 59.983 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.616 | 59.983 |  | 1 | 0 | 1 | 0 | 0
40626.6161 | 59.98 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.6161 | 59.981 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6161 | 59.983 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6161 | 59.987 |  | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.6162 | 59.988 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6162 | 59.987 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6162 | 59.991 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6162 | 59.988 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.6162 | 59.986 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6163 | 59.988 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6163 | 59.996 |  | 1 | 0 | 1 | 0.0079994 | 0.0079994
40626.6163 | 60.003 |  | 1 | 1 | 1 | 0.007 | 0.007
40626.6163 | 60.007 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6164 | 60.007 |  | 1 | 1 | 1 | 0 | 0
40626.6164 | 60.006 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6164 | 60.005 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6164 | 60.004 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6165 | 60.003 |  | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.6165 | 60.004 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6165 | 60.005 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6165 | 60.01 |  | 1 | 1 | 1 | 0.0049973 | 0.0049973
40626.6166 | 60.016 |  | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.6166 | 60.023 |  | 1 | 1 | 1 | 0.007 | 0.007
40626.6166 | 60.022 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6166 | 60.021 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6166 | 60.02 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6167 | 60.018 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6167 | 60.017 |  | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.6167 | 60.016 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6167 | 60.015 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6168 | 60.016 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6168 | 60.017 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6168 | 60.015 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6168 | 60.012 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6169 | 60.011 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6169 | 60.009 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6169 | 60.004 |  | 1 | 1 | 1 | -0.0049973 | 0.0049973
40626.6169 | 59.999 |  | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.6169 | 59.995 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.617 | 59.994 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.617 | 59.991 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.617 | 59.991 |  | 1 | 0 | 1 | 0 | 0
40626.617 | 59.989 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6171 | 59.987 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6171 | 59.984 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6171 | 59.984 |  | 1 | 0 | 1 | 0 | 0
40626.6171 | 59.988 |  | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.6172 | 59.995 |  | 1 | 0 | 1 | 0.007 | 0.007
40626.6172 | 60.003 |  | 1 | 1 | 1 | 0.0079994 | 0.0079994
40626.6172 | 60.007 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6172 | 60.007 |  | 1 | 1 | 1 | 0 | 0
40626.6172 | 60.002 |  | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.6173 | 60.003 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6173 | 60.005 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6173 | 60.007 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6173 | 60.006 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6174 | 60.006 |  | 1 | 1 | 1 | 0 | 0
40626.6174 | 60.009 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6174 | 60.009 |  | 1 | 1 | 1 | 0 | 0
40626.6174 | 60.009 |  | 1 | 1 | 1 | 0 | 0
40626.6175 | 60.015 |  | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.6175 | 60.022 |  | 1 | 1 | 1 | 0.007 | 0.007
40626.6175 | 60.022 |  | 1 | 1 | 1 | 0 | 0
40626.6175 | 60.019 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6175 | 60.017 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6176 | 60.016 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6176 | 60.016 |  | 1 | 1 | 1 | 0 | 0
40626.6176 | 60.017 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6176 | 60.02 |  | 1 | 1 | 1 | 0.0030022 | 0.0030022
40626.6177 | 60.024 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.6177 | 60.024 |  | 1 | 1 | 1 | 0 | 0
40626.6177 | 60.023 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6177 | 60.023 |  | 1 | 1 | 1 | 0 | 0
40626.6178 | 60.015 |  | 1 | 1 | 1 | -0.0079994 | 0.0079994
40626.6178 | 60.01 |  | 1 | 1 | 1 | -0.0050011 | 0.0050011
40626.6178 | 60.008 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6178 | 60.006 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6178 | 60.006 |  | 1 | 1 | 1 | 0 | 0
40626.6179 | 60.003 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6179 | 60.002 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6179 | 60.003 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6179 | 60.002 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.618 | 60.004 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.618 | 60.003 |  | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.618 | 60 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.618 | 59.996 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.6181 | 59.99 |  | 1 | 0 | 1 | -0.0059967 | 0.0059967
40626.6181 | 59.99 |  | 1 | 0 | 1 | 0 | 0
40626.6181 | 59.985 |  | 1 | 0 | 1 | -0.0050011 | 0.0050011
40626.6181 | 59.983 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6181 | 59.981 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6182 | 59.983 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6182 | 59.987 |  | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.6182 | 59.987 |  | 1 | 0 | 1 | 0 | 0
40626.6182 | 59.988 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6183 | 59.988 |  | 1 | 0 | 1 | 0 | 0
40626.6183 | 59.989 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6183 | 59.99 |  | 1 | 0 | 1 | 0.0010033 | 0.0010033
40626.6183 | 59.989 |  | 1 | 0 | 1 | -0.0010033 | 0.0010033
40626.6184 | 59.986 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6184 | 59.982 |  | 1 | 0 | 1 | -0.0040016 | 0.0040016
40626.6184 | 59.984 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6184 | 59.988 |  | 1 | 0 | 1 | 0.0039978 | 0.0039978
40626.6184 | 59.992 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6185 | 59.997 |  | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.6185 | 60.005 |  | 1 | 1 | 1 | 0.0079994 | 0.0079994
40626.6185 | 60.012 |  | 1 | 1 | 1 | 0.007 | 0.007
40626.6185 | 60.017 |  | 1 | 1 | 1 | 0.0049973 | 0.0049973
40626.6186 | 60.021 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6186 | 60.022 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6186 | 60.02 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6186 | 60.017 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6187 | 60.017 |  | 1 | 1 | 1 | 0 | 0
40626.6187 | 60.017 |  | 1 | 1 | 1 | 0 | 0
40626.6187 | 60.018 |  | 1 | 1 | 1 | 0.0010033 | 0.0010033
40626.6187 | 60.022 |  | 1 | 1 | 1 | 0.0039978 | 0.0039978
40626.6188 | 60.021 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6188 | 60.023 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6188 | 60.02 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6188 | 60.018 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6188 | 60.015 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6189 | 60.016 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6189 | 60.017 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6189 | 60.019 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6189 | 60.02 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.619 | 60.017 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.619 | 60.015 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.619 | 60.012 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.619 | 60.009 |  | 1 | 1 | 1 | -0.0030022 | 0.0030022
40626.6191 | 60.009 |  | 1 | 1 | 1 | 0 | 0
40626.6191 | 60.008 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6191 | 60.009 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6191 | 60.01 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6191 | 60.012 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6192 | 60.013 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6192 | 60.012 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6192 | 60.015 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6192 | 60.02 |  | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.6193 | 60.022 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6193 | 60.02 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6193 | 60.019 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6193 | 60.018 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6194 | 60.018 |  | 1 | 1 | 1 | 0 | 0
40626.6194 | 60.018 |  | 1 | 1 | 1 | 0 | 0
40626.6194 | 60.016 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6194 | 60.015 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6194 | 60.013 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6195 | 60.011 |  | 1 | 1 | 1 | -0.0019989 | 0.0019989
40626.6195 | 60.005 |  | 1 | 1 | 1 | -0.0060005 | 0.0060005
40626.6195 | 60.001 |  | 1 | 1 | 1 | -0.0040016 | 0.0040016
40626.6195 | 59.998 |  | 1 | 0 | 1 | -0.0029984 | 0.0029984
40626.6196 | 59.996 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6196 | 59.997 |  | 1 | 0 | 1 | 0.0010033 | 0.0010033
40626.6196 | 59.998 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6196 | 60 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6197 | 60.003 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6197 | 59.999 |  | 1 | 0 | 1 | -0.0039978 | 0.0039978
40626.6197 | 60.001 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6197 | 59.986 |  | 1 | 0 | 1 | -0.014999 | 0.014999
40626.6197 | 59.974 |  | 1 | 0 | 1 | -0.012001 | 0.012001
40626.6198 | 59.969 |  | 1 | 0 | 1 | -0.0049973 | 0.0049973
40626.6198 | 59.967 |  | 1 | 0 | 1 | -0.0020027 | 0.0020027
40626.6198 | 59.968 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6198 | 59.968 |  | 1 | 0 | 1 | 0 | 0
40626.6199 | 59.966 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.6199 | 59.967 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6199 | 59.968 |  | 1 | 0 | 1 | 0.00099945 | 0.00099945
40626.6199 | 59.966 |  | 1 | 0 | 1 | -0.0019989 | 0.0019989
40626.62 | 59.965 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.62 | 59.964 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.62 | 59.964 |  | 1 | 0 | 1 | 0 | 0
40626.62 | 59.961 |  | 1 | 0 | 1 | -0.0030022 | 0.0030022
40626.62 | 59.963 |  | 1 | 0 | 1 | 0.0020027 | 0.0020027
40626.6201 | 59.972 |  | 1 | 0 | 1 | 0.0089989 | 0.0089989
40626.6201 | 59.971 |  | 1 | 0 | 1 | -0.00099945 | 0.00099945
40626.6201 | 59.976 |  | 1 | 0 | 1 | 0.0050011 | 0.0050011
40626.6201 | 59.978 |  | 1 | 0 | 1 | 0.0019989 | 0.0019989
40626.6202 | 59.978 |  | 1 | 0 | 1 | 0 | 0
40626.6202 | 59.981 |  | 1 | 0 | 1 | 0.0029984 | 0.0029984
40626.6202 | 59.985 |  | 1 | 0 | 1 | 0.0040016 | 0.0040016
40626.6202 | 59.991 |  | 1 | 0 | 1 | 0.0060005 | 0.0060005
40626.6203 | 59.996 |  | 1 | 0 | 1 | 0.0049973 | 0.0049973
40626.6203 | 60.002 |  | 1 | 1 | 1 | 0.0060005 | 0.0060005
40626.6203 | 60.007 |  | 1 | 1 | 1 | 0.0050011 | 0.0050011
40626.6203 | 60.007 |  | 1 | 1 | 1 | 0 | 0
40626.6203 | 60.008 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6204 | 60.008 |  | 1 | 1 | 1 | 0 | 0
40626.6204 | 60.009 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6204 | 60.01 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6204 | 60.01 |  | 1 | 1 | 1 | 0 | 0
40626.6205 | 60.014 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6205 | 60.014 |  | 1 | 1 | 1 | 0 | 0
40626.6205 | 60.016 |  | 1 | 1 | 1 | 0.0019989 | 0.0019989
40626.6205 | 60.023 |  | 1 | 1 | 1 | 0.007 | 0.007
40626.6206 | 60.027 |  | 1 | 1 | 1 | 0.0040016 | 0.0040016
40626.6206 | 60.027 |  | 1 | 1 | 1 | 0 | 0
40626.6206 | 60.03 |  | 1 | 1 | 1 | 0.0029984 | 0.0029984
40626.6206 | 60.03 |  | 1 | 1 | 1 | 0 | 0
40626.6206 | 60.03 |  | 1 | 1 | 1 | 0 | 0
40626.6207 | 60.032 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027
40626.6207 | 60.031 |  | 1 | 1 | 1 | -0.0010033 | 0.0010033
40626.6207 | 60.028 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6207 | 60.029 |  | 1 | 1 | 1 | 0.00099945 | 0.00099945
40626.6208 | 60.026 |  | 1 | 1 | 1 | -0.0029984 | 0.0029984
40626.6208 | 60.025 |  | 1 | 1 | 1 | -0.00099945 | 0.00099945
40626.6208 | 60.023 |  | 1 | 1 | 1 | -0.0020027 | 0.0020027
40626.6208 | 60.025 |  | 1 | 1 | 1 | 0.0020027 | 0.0020027

## Initial & Sustained Graph
Graph and Analysis Alignment
Rows of Data to Shift
1 | Positive values shift data to right
Negative values shift data to left
Note on P5: Adjust this value to align the frequency event in the center of the graph on the dark vertical grid line. The first change in frequency of the event should occur on the center vertical grid line on the graph. To move the frequency to the right, increase this value. To move the frequency data to the left, decrease this value.

## Evaluation
scan rate | 2 | seconds |  |  | Date: | 2011-03-24 13:59 | Auto |  |  | Unit:Generator x | [11 empty] | Auto
[5 empty] | Time of T(0) | 40626.5827 | 310 |  |  | Grid Nominal Frequency | 60 | Hz | [9 empty] | Manual
[5 empty] | Time of Frequency Recovery to 60 Hz +/- Governor Deadband | 40626.5853 | 500 |  |  | Turbine NDC (HSL) | 550 | MW
[5 empty] | Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0024 | Hz |  |  | Droop Setting | 5% | 3 | Hz
[5 empty] | Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8206 | Hz |  |  | Deadband Setting | 0.017 | Hz
[5 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.18179 | Hz |  |  | Hz Span | 2.983 | Hz
[5 empty] | Pre-Perturbation Average MW [T(-2 ) to T(-16)] | 530.1148 | MW |  |  | Governor Type | Digital
[5 empty] | Post-Perturbation Average MW [T(+20 to T(+52)] | 543.7391 | MW |  |  | Prime Mover | Steam Turbine
[5 empty] | Pre to Post Perturbation Delta MW Actual Adj for Ramp | 16.4944 | MW |  |  | Steam Pressure Curve | PSI (1) | MW (1) |  | PSI (2) | MW (2) | PSI (3) | MW (3) | PSI (4) | MW (4) | PSI (5) | MW (5)
[5 empty] | Initial Performance Ramp Magnitude Adjustment | -2.8701 | MW |  |  | Rated Throttle Pressure | 2400 | 350 |  | 2000 | 300 | 1800 | 250 | 1600 | 200 | 1400 | 100
[5 empty] | EPFR(@Droop & DB)PRE | 0 | MW |  |  | Minimum Throttle Pressure | 1200 | 50
[5 empty] | EPFR(@Droop & DB)POST | 29.9451 | MW |  |  | K (Limiting Factor) | 0.24 | PSI Change/MW Change (allowable range of value 0 to 0.6)
[5 empty] | EPFR(@Droop & DB)Delta | 29.9451 | MW |  |  | TC (frequency response filter constant) | 0.13 | Time Constant for delayed delivery of PFR during Sustained Measure
[5 empty] | % Steam Flow | 98.86% |  |  |  | Maximum operating level (HSL) less Power Augmentation | 550 | MW
[5 empty] | Steam Flow Change Factor | 1.9772 |  |  |  | Minimum operating level (LSL) | 140 | MW
[5 empty] | MW Adjustment | -3.2565 | MW |  |  | Low Hz | Delta Hz Event
[5 empty] | Throttle Pressure | 2400 | PSI
[5 empty] | Throttle Pressure % of Rated | 100%
[5 empty] | EPFR(Final) | 26.6887 | MW
[5 empty] | MW Response in right direction for frequency delta | Yes |  |  |  | 530.5581 | Actual MW @ T(-4)
[5 empty] | Up Headroom % | 3.615% |  |  |  | 20.6134 | Starting and Ending Difference in MW output during the event recovery period (indicates ramp direction during recovery period)
[5 empty] | Down Headroom % | 70.93% |  |  |  | 0:04 | Target Model Period (h:mm:ss)
[5 empty] | Up Headroom MW | 19.8852 | MW |  |  | 59.815 | Post-Perturbation Frequency @T(+46)
[5 empty] | Down Headroom MW | -389.7286 | MW |  |  | 30.9758 | ESPFR(@Droop & DB@T(+46)
[5 empty] | Is EPFR(Final) Headroom Available | No |  |  |  | -3.3822 | MW Adjustment @ T(+46)
[5 empty] | Is Headroom greater than 2% or 5 MW | Yes |  |  |  | -3.9938 | Pre Perturbation Ramp Magnitude Adjustment @T(+46)
[5 empty] | Pre to Post Perturbation Delta Frequency Actual @t(+46) | -0.18738 | Hz |  |  | 30.9758 | ESPFR(@Droop & DB@T(+46) Delta
[5 empty] | % Steam Flow@T(+46) | 99.26% |  |  |  | 27.5936 | ESPFR(Final@T(+46))
[5 empty] | Steam Flow Change Factor@T(+46) | 1.9852 |  |  |  | 545.9412 | Post-Perturbation Max MW(low Hz) Min MW(high Hz) [T(+46 to T(+60)]
[5 empty] | Power Augmentation Capacity | 0 |  |  |  | 19.8202 | Pre to Post Perturbation @T(+46) Delta MW Actual Adjusted for Ramp
[10 empty] | Yes | MW Response in right direction for frequency delta@T(+46)
[10 empty] | No | Is ESPFR(Final@T(+46) Headroom Available
[5 empty] | Initial Response P.U. Performance | 0.75 | P.U. (R9) |  | (R10) | 0.75 | P.U. Sustianed Response P.U. Performance
Initial
[7 empty] | (EPFR) |  |  | Measure
[7 empty] | Ideal | (TC) | (Limiting Factor) | Final
[7 empty] | Expected | Delayed | Adjustment | Expected |  | Model |  |  | Model
|  |  | Generator |  |  |  | Primary | Delivery | for Throttle | Primary | Average | Period |  |  | Period
|  | Frequency | Output | Average | Average |  | Frequency | Frequency | Pressure | Frequency | Ramp | Target |  |  | Ramp
| T | Hz | MW | Frequency | MW | HSL | Response | Response | Change | Response | MW/scan | MW |  |  | MW
T-72 sec | 40626.5819 | 60.013 | 535.7023 |  |  | 550 | 0 | 0 | 0.031201
T-70 sec | 40626.5819 | 60.012 | 534.7816 |  |  | 550 | 0 | 0 | 0.028802
T-68 sec | 40626.5819 | 60.013 | 534.7816 |  |  | 550 | 0 | 0 | 0.031201
T-66 sec | 40626.582 | 60.013 | 535.0607 |  |  | 550 | 0 | 0 | 0.031201
T-64 sec | 40626.582 | 60.013 | 535.0607 |  |  | 550 | 0 | 0 | 0.031201
T-62 sec | 40626.582 | 60.013 | 535.4227 |  |  | 550 | 0 | 0 | 0.031201
T-60 sec | 40626.582 | 60.028 | 535.4227 |  |  | 550 | -2.0281 | -0.26366 | 0.0672 |  | -0.18743 | 535.4227
T-58 sec | 40626.5821 | 60.035 | 534.8942 |  |  | 550 | -3.3188 | -0.66082 | 0.084 |  | -0.18743 | 534.8381
T-56 sec | 40626.5821 | 60.039 | 534.8942 |  |  | 550 | -4.0566 | -1.1023 | 0.093604 |  | -0.18743 | 534.2092
T-54 sec | 40626.5821 | 60.039 | 536.0845 |  |  | 550 | -4.0566 | -1.4863 | 0.093604 |  | -0.18743 | 533.6377
T-52 sec | 40626.5821 | 60.038 | 536.0845 |  |  | 550 | -3.8716 | -1.7964 | 0.091196 |  | -0.18743 | 533.1402
T-50 sec | 40626.5822 | 60.031 | 534.3259 |  |  | 550 | -2.581 | -1.8984 | 0.074396 |  | -0.18743 | 532.8508
T-48 sec | 40626.5822 | 60.031 | 534.3259 |  |  | 550 | -2.581 | -1.9871 | 0.074396 |  | -0.18743 | 532.5746
T-46 sec | 40626.5822 | 60.029 | 534.3387 |  |  | 550 | -2.2124 | -2.0164 | 0.069598 |  | -0.18743 | 532.3579
T-44 sec | 40626.5822 | 60.028 | 534.3387 |  |  | 550 | -2.0281 | -2.018 | 0.0672 |  | -0.18743 | 532.169
T-42 sec | 40626.5822 | 60.028 | 534.5214 |  |  | 550 | -2.0281 | -2.0193 | 0.0672 |  | -0.18743 | 531.9802
T-40 sec | 40626.5823 | 60.029 | 534.5214 |  |  | 550 | -2.2124 | -2.0444 | 0.069598 |  | -0.18743 | 531.7677
T-38 sec | 40626.5823 | 60.028 | 533.7285 |  |  | 550 | -2.0281 | -2.0423 | 0.0672 |  | -0.18743 | 531.5824
T-36 sec | 40626.5823 | 60.028 | 533.7285 |  |  | 550 | -2.0281 | -2.0404 | 0.0672 |  | -0.18743 | 531.3968
T-34 sec | 40626.5823 | 60.028 | 533.5816 |  |  | 550 | -2.0281 | -2.0388 | 0.0672 |  | -0.18743 | 531.211
T-32 sec | 40626.5824 | 60.031 | 533.5816 |  |  | 550 | -2.581 | -2.1093 | 0.074396 |  | -0.18743 | 530.9531
T-30 sec | 40626.5824 | 60.03 | 532.539 |  |  | 550 | -2.3967 | -2.1467 | 0.071997 |  | -0.18743 | 530.7283
T-28 sec | 40626.5824 | 60.028 | 532.539 |  |  | 550 | -2.0281 | -2.1313 | 0.0672 |  | -0.18743 | 530.5563
T-26 sec | 40626.5824 | 60.027 | 532.505 |  |  | 550 | -1.8439 | -2.0939 | 0.064801 |  | -0.18743 | 530.4062
T-24 sec | 40626.5825 | 60.03 | 532.505 |  |  | 550 | -2.3967 | -2.1333 | 0.071997 |  | -0.18743 | 530.1794
T-22 sec | 40626.5825 | 60.025 | 531.8575 |  |  | 550 | -1.4753 | -2.0477 | 0.060004 |  | -0.18743 | 530.0775
T-20 sec | 40626.5825 | 60.019 | 531.8575 |  |  | 550 | -0.36894 | -1.8295 | 0.045602 |  | -0.18743 | 530.1083
T-18 sec | 40626.5825 | 60.016 | 531.4795 |  |  | 550 | 0 | -1.5917 | 0.038397 |  | -0.18743 | 530.1587
T-16 sec | 40626.5825 | 60.011 | 531.4795 | 60.0024 | 530.1148 | 550 | 0 | -1.3847 | 0.026404 |  | -0.18743 | 530.1782
T-14 sec | 40626.5826 | 60.008 | 530.5207 | 60.0024 | 530.1148 | 550 | 0 | -1.2047 | 0.019199 |  | -0.18743 | 530.1708
T-12 sec | 40626.5826 | 60.006 | 530.5207 | 60.0024 | 530.1148 | 550 | 0 | -1.0481 | 0.014401 |  | -0.18743 | 530.14
T-10 sec | 40626.5826 | 60.003 | 528.7762 | 60.0024 | 530.1148 | 550 | 0 | -0.91185 | 0.007196 |  | -0.18743 | 530.0888
T-08 sec | 40626.5826 | 60 | 528.7762 | 60.0024 | 530.1148 | 550 | 0 | -0.79331 | 0 |  | -0.18743 | 530.0199
T-06 sec | 40626.5827 | 59.998 | 530.5581 | 60.0024 | 530.1148 | 550 | 0 | -0.69018 | -0.0047974 |  | -0.18743 | 529.9356
T-04 sec | 40626.5827 | 59.996 | 530.5581 | 60.0024 | 530.1148 | 550 | 0 | -0.60046 | -0.0096039 |  | -0.18743 | 529.8379
T-02 sec | 40626.5827 | 59.997 | 529.7286 | 60.0024 | 530.1148 | 550 | 0 | -0.5224 | -0.007196 |  | -0.18743 | 529.7286
T+0 sec | 40626.5827 | 59.977 | 529.7286 |  |  | 550 | 1.106 | -0.3107 | -0.055197 |  | 0 | 529.9403
T+02 sec | 40626.5828 | 59.863 | 529.7286 |  |  | 550 | 22.1256 | 2.606 | -0.3288 |  | 0.18739 | 533.0444 |  |  | 531.346
T+04 sec | 40626.5828 | 59.863 | 529.7286 |  |  | 550 | 22.1256 | 5.1436 | -0.3288 |  | 0.18739 | 535.7693 |  |  | 531.5334
T+06 sec | 40626.5828 | 59.814 | 530.0621 |  |  | 550 | 31.1601 | 8.5257 | -0.4464 |  | 0.18739 | 539.3389 |  |  | 531.7207
T+08 sec | 40626.5828 | 59.799 | 534.4206 |  |  | 550 | 33.9256 | 11.8277 | -0.4824 |  | 0.18739 | 542.8282 |  |  | 531.9081
T+10 sec | 40626.5828 | 59.799 | 534.4206 |  |  | 550 | 33.9256 | 14.7004 | -0.4824 |  | 0.18739 | 545.8884 |  |  | 532.0955
T+12 sec | 40626.5829 | 59.801 | 544.002 |  |  | 550 | 33.5571 | 17.1518 | -0.4776 |  | 0.18739 | 548.5271 |  |  | 532.2829
T+14 sec | 40626.5829 | 59.8 | 544.002 |  |  | 550 | 33.7413 | 19.3084 | -0.48 |  | 0.18739 | 550 |  |  | 532.4703
T+16 sec | 40626.5829 | 59.803 | 548.178 |  |  | 550 | 33.1878 | 21.1127 | -0.4728 |  | 0.18739 | 550 |  |  | 532.6577
T+18 sec | 40626.5829 | 59.808 | 548.178 |  |  | 550 | 32.2664 | 22.5627 | -0.4608 |  | 0.18739 | 550 |  |  | 532.8451
T+20 sec | 40626.583 | 59.81 | 546.6487 | 59.8206 | 543.7391 | 550 | 31.8972 | 23.7762 | -0.456 | 547.1299 | 0.18739 | 550 |  |  | 533.0325
T+22 sec | 40626.583 | 59.817 | 546.6487 | 59.8206 | 543.7391 | 550 | 30.6065 | 24.6641 | -0.4392 | 547.1299 | 0.18739 | 550 |  |  | 533.2199
T+24 sec | 40626.583 | 59.824 | 544.5483 | 59.8206 | 543.7391 | 550 | 29.3159 | 25.2689 | -0.4224 | 547.1299 | 0.18739 | 550 |  |  | 533.4073
T+26 sec | 40626.583 | 59.824 | 544.5483 | 59.8206 | 543.7391 | 550 | 29.3159 | 25.795 | -0.4224 | 547.1299 | 0.18739 | 550 |  |  | 533.5947
T+28 sec | 40626.5831 | 59.827 | 541.8083 | 59.8206 | 543.7391 | 550 | 28.7631 | 26.1808 | -0.4152 | 547.1299 | 0.18739 | 550 |  |  | 533.7821
T+30 sec | 40626.5831 | 59.827 | 541.8083 | 59.8206 | 543.7391 | 550 | 28.7631 | 26.5165 | -0.4152 | 547.1299 | 0.18739 | 550 |  |  | 533.9695
T+32 sec | 40626.5831 | 59.828 | 539.9456 | 59.8206 | 543.7391 | 550 | 28.5788 | 26.7846 | -0.4128 | 547.1299 | 0.18739 | 550 |  |  | 534.1569
T+34 sec | 40626.5831 | 59.826 | 539.9456 | 59.8206 | 543.7391 | 550 | 28.9473 | 27.0658 | -0.4176 | 547.1299 | 0.18739 | 550 |  |  | 534.3443
T+36 sec | 40626.5831 | 59.823 | 541.4998 | 59.8206 | 543.7391 | 550 | 29.5002 | 27.3822 | -0.4248 | 547.1299 | 0.18739 | 550 |  |  | 534.5316
T+38 sec | 40626.5832 | 59.824 | 541.4998 | 59.8206 | 543.7391 | 550 | 29.3159 | 27.6336 | -0.4224 | 547.1299 | 0.18739 | 550 |  |  | 534.719
T+40 sec | 40626.5832 | 59.822 | 543.3224 | 59.8206 | 543.7391 | 550 | 29.6851 | 27.9003 | -0.4272 | 547.1299 | 0.18739 | 550 |  |  | 534.9064
T+42 sec | 40626.5832 | 59.818 | 543.3224 | 59.8206 | 543.7391 | 550 | 30.4222 | 28.2282 | -0.4368 | 547.1299 | 0.18739 | 550 |  |  | 535.0938
T+44 sec | 40626.5832 | 59.818 | 545.1118 | 59.8206 | 543.7391 | 550 | 30.4222 | 28.5134 | -0.4368 | 547.1299 | 0.18739 | 550 |  |  | 535.2812
T+46 sec | 40626.5833 | 59.815 | 545.1118 | 59.8206 | 543.7391 | 550 | 30.9758 | 28.8335 | -0.444 | 547.1299 | 0.18739 | 550 |  |  | 535.4686 | 553.7145
T+48 sec | 40626.5833 | 59.812 | 545.9412 | 59.8206 | 543.7391 | 550 | 31.5286 | 29.1839 | -0.4512 | 547.1299 | 0.18739 | 550 |  |  | 535.656 | 553.7145
T+50 sec | 40626.5833 | 59.815 | 545.9412 | 59.8206 | 543.7391 | 550 | 30.9758 | 29.4168 | -0.444 | 547.1299 | 0.18739 | 550 |  |  | 535.8434 | 553.7145
T+52 sec | 40626.5833 | 59.82 | 545.9116 | 59.8206 | 543.7391 | 550 | 30.0537 | 29.4996 | -0.432 | 547.1299 | 0.18739 | 550 |  |  | 536.0308 | 553.7145
T+54 sec | 40626.5834 | 59.819 | 545.9116 |  |  | 550 | 30.238 | 29.5956 | -0.4344 |  | 0.18739 | 550 |  |  | 536.2182 | 553.7145
T+56 sec | 40626.5834 | 59.819 | 544.8771 |  |  | 550 | 30.238 | 29.6791 | -0.4344 |  | 0.18739 | 550 |  |  | 536.4056 | 553.7145
T+58 sec | 40626.5834 | 59.819 | 544.8771 |  |  | 550 | 30.238 | 29.7518 | -0.4344 |  | 0.18739 | 550 |  |  | 536.593 | 553.7145
T+60 sec | 40626.5834 | 59.821 | 544.639 |  |  | 550 | 29.8694 | 29.7671 | -0.4296 |  | 0.18739 | 550 |  |  | 536.7804 | 553.7145
| 40626.5834 | 59.825 | 544.639 |  |  | 550 | 29.1316 | 29.6844 | -0.42 |  | 0.18739 | 550 |  |  | 536.9678
| 40626.5835 | 59.83 | 545.9454 |  |  | 550 | 28.2095 | 29.4927 | -0.408 |  | 0.18739 | 549.9957 |  |  | 537.1552
| 40626.5835 | 59.831 | 545.9454 |  |  | 550 | 28.0252 | 29.3019 | -0.4056 |  | 0.18739 | 549.9923 |  |  | 537.3425
| 40626.5835 | 59.839 | 544.6492 |  |  | 550 | 26.5503 | 28.9442 | -0.3864 |  | 0.18739 | 549.822 |  |  | 537.5299
| 40626.5835 | 59.839 | 544.6492 |  |  | 550 | 26.5503 | 28.633 | -0.3864 |  | 0.18739 | 549.6981 |  |  | 537.7173
| 40626.5836 | 59.842 | 543.997 |  |  | 550 | 25.9975 | 28.2904 | -0.3792 |  | 0.18739 | 549.5429 |  |  | 537.9047
| 40626.5836 | 59.847 | 543.997 |  |  | 550 | 25.0754 | 27.8725 | -0.3672 |  | 0.18739 | 549.3124 |  |  | 538.0921
| 40626.5836 | 59.846 | 544.2888 |  |  | 550 | 25.2597 | 27.5328 | -0.3696 |  | 0.18739 | 549.1601 |  |  | 538.2795
| 40626.5836 | 59.845 | 544.2888 |  |  | 550 | 25.444 | 27.2612 | -0.372 |  | 0.18739 | 549.0759 |  |  | 538.4669
| 40626.5837 | 59.846 | 544.4759 |  |  | 550 | 25.2597 | 27.001 | -0.3696 |  | 0.18739 | 549.0031 |  |  | 538.6543
| 40626.5837 | 59.85 | 544.4759 |  |  | 550 | 24.5226 | 26.6788 | -0.36 |  | 0.18739 | 548.8683 |  |  | 538.8417
| 40626.5837 | 59.85 | 545.1849 |  |  | 550 | 24.5226 | 26.3985 | -0.36 |  | 0.18739 | 548.7754 |  |  | 539.0291
| 40626.5837 | 59.854 | 545.1849 |  |  | 550 | 23.7848 | 26.0587 | -0.3504 |  | 0.18739 | 548.623 |  |  | 539.2165
| 40626.5837 | 59.863 | 543.7529 |  |  | 550 | 22.1256 | 25.5474 | -0.3288 |  | 0.18739 | 548.2991 |  |  | 539.4039
| 40626.5838 | 59.867 | 543.7529 |  |  | 550 | 21.3878 | 25.0067 | -0.3192 |  | 0.18739 | 547.9457 |  |  | 539.5913
| 40626.5838 | 59.867 | 543.9365 |  |  | 550 | 21.3878 | 24.5362 | -0.3192 |  | 0.18739 | 547.6627 |  |  | 539.7787
| 40626.5838 | 59.874 | 543.9365 |  |  | 550 | 20.0971 | 23.9591 | -0.3024 |  | 0.18739 | 547.273 |  |  | 539.9661
| 40626.5838 | 59.875 | 542.6066 |  |  | 550 | 19.9128 | 23.4331 | -0.3 |  | 0.18739 | 546.9344 |  |  | 540.1534
| 40626.5839 | 59.881 | 542.6066 |  |  | 550 | 18.8065 | 22.8316 | -0.2856 |  | 0.18739 | 546.5203 |  |  | 540.3408
| 40626.5839 | 59.881 | 542.5233 |  |  | 550 | 18.8065 | 22.3084 | -0.2856 |  | 0.18739 | 546.1844 |  |  | 540.5282
| 40626.5839 | 59.887 | 542.5233 |  |  | 550 | 17.7001 | 21.7093 | -0.2712 |  | 0.18739 | 545.7727 |  |  | 540.7156
| 40626.5839 | 59.891 | 544.5529 |  |  | 550 | 16.963 | 21.0923 | -0.2616 |  | 0.18739 | 545.3431 |  |  | 540.903
| 40626.584 | 59.902 | 544.5529 |  |  | 550 | 14.9346 | 20.2918 | -0.2352 |  | 0.18739 | 544.73 |  |  | 541.0904
| 40626.584 | 59.9 | 545.1033 |  |  | 550 | 15.3031 | 19.6432 | -0.24 |  | 0.18739 | 544.2689 |  |  | 541.2778
| 40626.584 | 59.9 | 545.1033 |  |  | 550 | 15.3031 | 19.079 | -0.24 |  | 0.18739 | 543.892 |  |  | 541.4652
| 40626.584 | 59.899 | 545.5423 |  |  | 550 | 15.4881 | 18.6122 | -0.2424 |  | 0.18739 | 543.6126 |  |  | 541.6526
| 40626.5841 | 59.899 | 545.5423 |  |  | 550 | 15.4881 | 18.2061 | -0.2424 |  | 0.18739 | 543.3939 |  |  | 541.84
| 40626.5841 | 59.902 | 546.4443 |  |  | 550 | 14.9346 | 17.7808 | -0.2352 |  | 0.18739 | 543.156 |  |  | 542.0274
| 40626.5841 | 59.912 | 546.4443 |  |  | 550 | 13.0911 | 17.1711 | -0.2112 |  | 0.18739 | 542.7337 |  |  | 542.2148
| 40626.5841 | 59.918 | 547.3142 |  |  | 550 | 11.9847 | 16.4969 | -0.1968 |  | 0.18739 | 542.2468 |  |  | 542.4022
| 40626.5841 | 59.918 | 547.3142 |  |  | 550 | 11.9847 | 15.9103 | -0.1968 |  | 0.18739 | 541.8477 |  |  | 542.5896
| 40626.5842 | 59.918 | 547.3142 |  |  | 550 | 11.9847 | 15.4 | -0.1968 |  | 0.18739 | 541.5247 |  |  | 542.777
| 40626.5842 | 59.923 | 548.6801 |  |  | 550 | 11.0626 | 14.8361 | -0.1848 |  | 0.18739 | 541.1483 |  |  | 542.9644
| 40626.5842 | 59.926 | 548.4333 |  |  | 550 | 10.5098 | 14.2737 | -0.1776 |  | 0.18739 | 540.7732 |  |  | 543.1517
| 40626.5842 | 59.924 | 548.4333 |  |  | 550 | 10.8783 | 13.8323 | -0.1824 |  | 0.18739 | 540.5192 |  |  | 543.3391
| 40626.5843 | 59.928 | 549.0335 |  |  | 550 | 10.1405 | 13.3524 | -0.1728 |  | 0.18739 | 540.2267 |  |  | 543.5265
| 40626.5843 | 59.93 | 549.0335 |  |  | 550 | 9.772 | 12.8869 | -0.168 |  | 0.18739 | 539.9486 |  |  | 543.7139
| 40626.5843 | 59.93 | 549.2899 |  |  | 550 | 9.772 | 12.482 | -0.168 |  | 0.18739 | 539.7311 |  |  | 543.9013
| 40626.5843 | 59.931 | 549.2899 |  |  | 550 | 9.5877 | 12.1057 | -0.1656 |  | 0.18739 | 539.5422 |  |  | 544.0887
| 40626.5844 | 59.933 | 550.1923 |  |  | 550 | 9.2192 | 11.7305 | -0.1608 |  | 0.18739 | 539.3544 |  |  | 544.2761
| 40626.5844 | 59.936 | 550.1923 |  |  | 550 | 8.6656 | 11.332 | -0.1536 |  | 0.18739 | 539.1433 |  |  | 544.4635
| 40626.5844 | 59.935 | 550.5021 |  |  | 550 | 8.8499 | 11.0094 | -0.156 |  | 0.18739 | 539.008 |  |  | 544.6509
| 40626.5844 | 59.938 | 550.5021 |  |  | 550 | 8.2971 | 10.6568 | -0.1488 |  | 0.18739 | 538.8428 |  |  | 544.8383
| 40626.5844 | 59.94 | 551.5063 |  |  | 550 | 7.9285 | 10.3021 | -0.144 |  | 0.18739 | 538.6756 |  |  | 545.0257
| 40626.5845 | 59.938 | 551.5063 |  |  | 550 | 8.2971 | 10.0414 | -0.1488 |  | 0.18739 | 538.6023 |  |  | 545.2131
| 40626.5845 | 59.938 | 552.3267 |  |  | 550 | 8.2971 | 9.8147 | -0.1488 |  | 0.18739 | 538.5629 |  |  | 545.4005
| 40626.5845 | 59.938 | 552.3267 |  |  | 550 | 8.2971 | 9.6174 | -0.1488 |  | 0.18739 | 538.553 |  |  | 545.5879
| 40626.5845 | 59.943 | 552.3267 |  |  | 550 | 7.375 | 9.3259 | -0.1368 |  | 0.18739 | 538.4489 |  |  | 545.7753
| 40626.5846 | 59.945 | 552.2819 |  |  | 550 | 7.0064 | 9.0243 | -0.132 |  | 0.18739 | 538.3348 |  |  | 545.9626
| 40626.5846 | 59.945 | 551.3163 |  |  | 550 | 7.0064 | 8.762 | -0.132 |  | 0.18739 | 538.2598 |  |  | 546.15
| 40626.5846 | 59.944 | 551.3163 |  |  | 550 | 7.1907 | 8.5577 | -0.1344 |  | 0.18739 | 538.243 |  |  | 546.3374
| 40626.5846 | 59.946 | 550.5966 |  |  | 550 | 6.8221 | 8.3321 | -0.1296 |  | 0.18739 | 538.2047 |  |  | 546.5248
| 40626.5847 | 59.951 | 550.5966 |  |  | 550 | 5.9001 | 8.0159 | -0.1176 |  | 0.18739 | 538.076 |  |  | 546.7122
| 40626.5847 | 59.953 | 549.5225 |  |  | 550 | 5.5315 | 7.693 | -0.1128 |  | 0.18739 | 537.9404 |  |  | 546.8996
| 40626.5847 | 59.954 | 549.5225 |  |  | 550 | 5.3472 | 7.388 | -0.1104 |  | 0.18739 | 537.8228 |  |  | 547.087
| 40626.5847 | 59.959 | 551.1065 |  |  | 550 | 4.4251 | 7.0028 | -0.098401 |  | 0.18739 | 537.625 |  |  | 547.2744
| 40626.5847 | 59.962 | 551.1065 |  |  | 550 | 3.8716 | 6.5958 | -0.091196 |  | 0.18739 | 537.4054 |  |  | 547.4618
| 40626.5848 | 59.964 | 550.8215 |  |  | 550 | 3.5031 | 6.1937 | -0.086398 |  | 0.18739 | 537.1907 |  |  | 547.6492
| 40626.5848 | 59.964 | 550.8215 |  |  | 550 | 3.5031 | 5.8439 | -0.086398 |  | 0.18739 | 537.0283 |  |  | 547.8366
| 40626.5848 | 59.963 | 551.5969 |  |  | 550 | 3.6873 | 5.5636 | -0.088797 |  | 0.18739 | 536.9354 |  |  | 548.024
| 40626.5848 | 59.963 | 551.5969 |  |  | 550 | 3.6873 | 5.3197 | -0.088797 |  | 0.18739 | 536.8788 |  |  | 548.2114
| 40626.5849 | 59.965 | 552.2954 |  |  | 550 | 3.3188 | 5.0596 | -0.084 |  | 0.18739 | 536.8061 |  |  | 548.3988
| 40626.5849 | 59.967 | 552.2954 |  |  | 550 | 2.9502 | 4.7853 | -0.079202 |  | 0.18739 | 536.7193 |  |  | 548.5862
| 40626.5849 | 59.97 | 552.7968 |  |  | 550 | 2.3967 | 4.4748 | -0.071997 |  | 0.18739 | 536.5962 |  |  | 548.7735
| 40626.5849 | 59.971 | 552.7968 |  |  | 550 | 2.2124 | 4.1807 | -0.069598 |  | 0.18739 | 536.4894 |  |  | 548.9609
| 40626.585 | 59.972 | 552.5348 |  |  | 550 | 2.0281 | 3.9009 | -0.0672 |  | 0.18739 | 536.397 |  |  | 549.1483
| 40626.585 | 59.97 | 552.5348 |  |  | 550 | 2.3967 | 3.7053 | -0.071997 |  | 0.18739 | 536.3889 |  |  | 549.3357
| 40626.585 | 59.972 | 552.3873 |  |  | 550 | 2.0281 | 3.4873 | -0.0672 |  | 0.18739 | 536.3582 |  |  | 549.5231
| 40626.585 | 59.974 | 552.3873 |  |  | 550 | 1.6596 | 3.2497 | -0.062402 |  | 0.18739 | 536.308 |  |  | 549.7105
| 40626.585 | 59.975 | 553.2163 |  |  | 550 | 1.4753 | 3.019 | -0.060004 |  | 0.18739 | 536.2647 |  |  | 549.8979
| 40626.5851 | 59.975 | 553.2163 |  |  | 550 | 1.4753 | 2.8183 | -0.060004 |  | 0.18739 | 536.2514 |  |  | 550.0853
| 40626.5851 | 59.976 | 551.8028 |  |  | 550 | 1.2903 | 2.6197 | -0.057596 |  | 0.18739 | 536.2402 |  |  | 550.2727
| 40626.5851 | 59.977 | 551.8028 |  |  | 550 | 1.106 | 2.4229 | -0.055197 |  | 0.18739 | 536.2308 |  |  | 550.4601
| 40626.5851 | 59.978 | 551.3834 |  |  | 550 | 0.92177 | 2.2278 | -0.052798 |  | 0.18739 | 536.223 |  |  | 550.6475
| 40626.5852 | 59.981 | 551.3834 |  |  | 550 | 0.36894 | 1.9861 | -0.045602 |  | 0.18739 | 536.1688 |  |  | 550.8349
| 40626.5852 | 59.983 | 552.4021 |  |  | 550 | 0 | 1.7279 | -0.040796 |  | 0.18739 | 536.098 |  |  | 551.0223
| 40626.5852 | 59.985 | 552.4021 |  |  | 550 | 0 | 1.5033 | -0.035999 |  | 0.18739 | 536.0608 |  |  | 551.2097
| 40626.5852 | 59.991 | 551.3555 |  |  | 550 | 0 | 1.3079 | -0.021597 |  | 0.18739 | 536.0527 |  |  | 551.3971
| 40626.5853 | 59.991 | 551.3555 |  |  | 550 | 0 | 1.1378 | -0.021597 |  | 0.18739 | 536.0701 |  |  | 551.5845
| 40626.5853 | 59.996 | 552.7619 |  |  | 550 | 0 | 0.98993 | -0.0096039 |  | 0.18739 | 536.1096 |  |  | 551.7718
| 40626.5853 | 60.002 | 552.7619 |  |  | 550 | 0 | 0.86124 | 0.0047974 |  | 0 | 535.9809 |  |  | 551.7718
| 40626.5853 | 60.004 | 551.6282 |  |  | 550 | 0 | 0.74928 | 0.0096039 |  | 0 | 535.8689 |  |  | 551.7718
| 40626.5853 | 60.005 | 551.6282 |  |  | 550 | 0 | 0.65187 | 0.012003 |  | 0 | 535.7715 |  |  | 551.7718
| 40626.5854 | 60.008 | 553.1126 |  |  | 550 | 0 | 0.56713 | 0.019199 |  | 0 | 535.6868 |  |  | 551.7718
| 40626.5854 | 60.014 | 553.1126 |  |  | 550 | 0 | 0.4934 | 0.0336 |  | 0 | 535.613 |  |  | 551.7718
| 40626.5854 | 60.019 | 554.8657 |  |  | 550 | -0.36894 | 0.3813 | 0.045602 |  | 0 | 535.5009 |  |  | 551.7718
| 40626.5854 | 60.022 | 554.8657 |  |  | 550 | -0.92177 | 0.2119 | 0.052798 |  | 0 | 535.3315 |  |  | 551.7718
| 40626.5855 | 60.029 | 553.5314 |  |  | 550 | -2.2124 | -0.10326 | 0.069598 |  | 0 | 535.0164 |  |  | 551.7718
| 40626.5855 | 60.033 | 553.5314 |  |  | 550 | -2.9502 | -0.47337 | 0.079202 |  | 0 | 534.6463 |  |  | 551.7718
| 40626.5855 | 60.038 | 554.5707 |  |  | 550 | -3.8716 | -0.91514 | 0.091196 |  | 0 | 534.2045 |  |  | 551.7718
| 40626.5855 | 60.034 | 554.5707 |  |  | 550 | -3.1345 | -1.2037 | 0.081601 |  | 0 | 533.916 |  |  | 551.7718
| 40626.5856 | 60.037 | 552.4359 |  |  | 550 | -3.6873 | -1.5265 | 0.088797 |  | 0 | 533.5931 |  |  | 551.7718
| 40626.5856 | 60.039 | 552.4359 |  |  | 550 | -4.0566 | -1.8554 | 0.093604 |  | 0 | 533.2642 |  |  | 551.7718
| 40626.5856 | 60.039 | 549.1614 |  |  | 550 | -4.0566 | -2.1416 | 0.093604 |  | 0 | 532.978 |  |  | 551.7718
| 40626.5856 | 60.042 | 549.1614 |  |  | 550 | -4.6094 | -2.4624 | 0.1008 |  | 0 | 532.6572 |  |  | 551.7718
| 40626.5856 | 60.041 | 547.9406 |  |  | 550 | -4.4251 | -2.7176 | 0.098401 |  | 0 | 532.4021 |  |  | 551.7718
| 40626.5857 | 60.043 | 547.9406 |  |  | 550 | -4.7937 | -2.9875 | 0.1032 |  | 0 | 532.1322 |  |  | 551.7718
| 40626.5857 | 60.041 | 549.3499 |  |  | 550 | -4.4251 | -3.1744 | 0.098401 |  | 0 | 531.9453 |  |  | 551.7718
| 40626.5857 | 60.043 | 549.3499 |  |  | 550 | -4.7937 | -3.3849 | 0.1032 |  | 0 | 531.7348 |  |  | 551.7718
| 40626.5857 | 60.044 | 548.9299 |  |  | 550 | -4.978 | -3.592 | 0.1056 |  | 0 | 531.5277 |  |  | 551.7718
| 40626.5858 | 60.046 | 548.9299 |  |  | 550 | -5.3472 | -3.8202 | 0.1104 |  | 0 | 531.2995 |  |  | 551.7718
| 40626.5858 | 60.043 | 549.8917 |  |  | 550 | -4.7937 | -3.9467 | 0.1032 |  | 0 | 531.1729 |  |  | 551.7718
| 40626.5858 | 60.038 | 549.8917 |  |  | 550 | -3.8716 | -3.937 | 0.091196 |  | 0 | 531.1827 |  |  | 551.7718
| 40626.5858 | 60.039 | 550.0666 |  |  | 550 | -4.0566 | -3.9525 | 0.093604 |  | 0 | 531.1671 |  |  | 551.7718
| 40626.5859 | 60.037 | 550.0666 |  |  | 550 | -3.6873 | -3.918 | 0.088797 |  | 0 | 531.2016 |  |  | 551.7718
| 40626.5859 | 60.034 | 550.5659 |  |  | 550 | -3.1345 | -3.8162 | 0.081601 |  | 0 | 531.3035 |  |  | 551.7718
| 40626.5859 | 60.036 | 550.5659 |  |  | 550 | -3.5031 | -3.7755 | 0.086398 |  | 0 | 531.3442 |  |  | 551.7718
| 40626.5859 | 60.034 | 550.2272 |  |  | 550 | -3.1345 | -3.6921 | 0.081601 |  | 0 | 531.4275 |  |  | 551.7718
| 40626.5859 | 60.036 | 550.2272 |  |  | 550 | -3.5031 | -3.6676 | 0.086398 |  | 0 | 531.4521 |  |  | 551.7718
| 40626.586 | 60.035 | 551.4907 |  |  | 550 | -3.3188 | -3.6222 | 0.084 |  | 0 | 531.4974 |  |  | 551.7718
| 40626.586 | 60.033 | 551.4907 |  |  | 550 | -2.9502 | -3.5349 | 0.079202 |  | 0 | 531.5848 |  |  | 551.7718
| 40626.586 | 60.039 | 551.1985 |  |  | 550 | -4.0566 | -3.6027 | 0.093604 |  | 0 | 531.517 |  |  | 551.7718
| 40626.586 | 60.041 | 551.1985 |  |  | 550 | -4.4251 | -3.7096 | 0.098401 |  | 0 | 531.41 |  |  | 551.7718
| 40626.5861 | 60.038 | 551.0989 |  |  | 550 | -3.8716 | -3.7307 | 0.091196 |  | 0 | 531.389 |  |  | 551.7718
| 40626.5861 | 60.034 | 551.0989 |  |  | 550 | -3.1345 | -3.6532 | 0.081601 |  | 0 | 531.4665 |  |  | 551.7718
| 40626.5861 | 60.031 | 551.5338 |  |  | 550 | -2.581 | -3.5138 | 0.074396 |  | 0 | 531.6059 |  |  | 551.7718
| 40626.5861 | 60.026 | 551.5338 |  |  | 550 | -1.6596 | -3.2727 | 0.062402 |  | 0 | 531.8469 |  |  | 551.7718
| 40626.5862 | 60.027 | 551.2632 |  |  | 550 | -1.8439 | -3.087 | 0.064801 |  | 0 | 532.0327 |  |  | 551.7718
| 40626.5862 | 60.026 | 551.2632 |  |  | 550 | -1.6596 | -2.9014 | 0.062402 |  | 0 | 532.2182 |  |  | 551.7718
| 40626.5862 | 60.026 | 550.0291 |  |  | 550 | -1.6596 | -2.74 | 0.062402 |  | 0 | 532.3797 |  |  | 551.7718
| 40626.5862 | 60.024 | 550.0291 |  |  | 550 | -1.2903 | -2.5515 | 0.057596 |  | 0 | 532.5681 |  |  | 551.7718
| 40626.5862 | 60.026 | 549.8652 |  |  | 550 | -1.6596 | -2.4356 | 0.062402 |  | 0 | 532.6841 |  |  | 551.7718
| 40626.5863 | 60.025 | 549.8652 |  |  | 550 | -1.4753 | -2.3107 | 0.060004 |  | 0 | 532.8089 |  |  | 551.7718
| 40626.5863 | 60.024 | 550.7635 |  |  | 550 | -1.2903 | -2.1781 | 0.057596 |  | 0 | 532.9416 |  |  | 551.7718
| 40626.5863 | 60.029 | 550.7635 |  |  | 550 | -2.2124 | -2.1825 | 0.069598 |  | 0 | 532.9371 |  |  | 551.7718
| 40626.5863 | 60.036 | 549.9413 |  |  | 550 | -3.5031 | -2.3542 | 0.086398 |  | 0 | 532.7654 |  |  | 551.7718
| 40626.5864 | 60.04 | 549.9413 |  |  | 550 | -4.2409 | -2.5995 | 0.096002 |  | 0 | 532.5202 |  |  | 551.7718
| 40626.5864 | 60.046 | 549.524 |  |  | 550 | -5.3472 | -2.9567 | 0.1104 |  | 0 | 532.163 |  |  | 551.7718
| 40626.5864 | 60.048 | 549.524 |  |  | 550 | -5.7158 | -3.3154 | 0.1152 |  | 0 | 531.8043 |  |  | 551.7718
| 40626.5864 | 60.047 | 548.0062 |  |  | 550 | -5.5315 | -3.6035 | 0.1128 |  | 0 | 531.5162 |  |  | 551.7718
| 40626.5865 | 60.046 | 548.0062 |  |  | 550 | -5.3472 | -3.8302 | 0.1104 |  | 0 | 531.2895 |  |  | 551.7718
| 40626.5865 | 60.044 | 547.0096 |  |  | 550 | -4.978 | -3.9794 | 0.1056 |  | 0 | 531.1403 |  |  | 551.7718
| 40626.5865 | 60.047 | 547.0096 |  |  | 550 | -5.5315 | -4.1811 | 0.1128 |  | 0 | 530.9385 |  |  | 551.7718
| 40626.5865 | 60.046 | 546.6521 |  |  | 550 | -5.3472 | -4.3327 | 0.1104 |  | 0 | 530.7869 |  |  | 551.7718
| 40626.5866 | 60.047 | 546.6521 |  |  | 550 | -5.5315 | -4.4886 | 0.1128 |  | 0 | 530.6311 |  |  | 551.7718
| 40626.5866 | 60.047 | 546.4784 |  |  | 550 | -5.5315 | -4.6242 | 0.1128 |  | 0 | 530.4955 |  |  | 551.7718
| 40626.5866 | 60.047 | 546.4784 |  |  | 550 | -5.5315 | -4.7421 | 0.1128 |  | 0 | 530.3775 |  |  | 551.7718
| 40626.5866 | 60.046 | 547.623 |  |  | 550 | -5.3472 | -4.8208 | 0.1104 |  | 0 | 530.2989 |  |  | 551.7718
| 40626.5866 | 60.049 | 547.623 |  |  | 550 | -5.9001 | -4.9611 | 0.1176 |  | 0 | 530.1586 |  |  | 551.7718
| 40626.5867 | 60.05 | 548.4683 |  |  | 550 | -6.0843 | -5.1071 | 0.12 |  | 0 | 530.0125 |  |  | 551.7718
| 40626.5867 | 60.049 | 548.4683 |  |  | 550 | -5.9001 | -5.2102 | 0.1176 |  | 0 | 529.9094 |  |  | 551.7718
| 40626.5867 | 60.047 | 548.267 |  |  | 550 | -5.5315 | -5.252 | 0.1128 |  | 0 | 529.8677 |  |  | 551.7718
| 40626.5867 | 60.043 | 548.267 |  |  | 550 | -4.7937 | -5.1924 | 0.1032 |  | 0 | 529.9272 |  |  | 551.7718
| 40626.5868 | 60.042 | 545.7502 |  |  | 550 | -4.6094 | -5.1166 | 0.1008 |  | 0 | 530.003 |  |  | 551.7718
| 40626.5868 | 60.038 | 545.7502 |  |  | 550 | -3.8716 | -4.9548 | 0.091196 |  | 0 | 530.1649 |  |  | 551.7718
| 40626.5868 | 60.038 | 547.5976 |  |  | 550 | -3.8716 | -4.8139 | 0.091196 |  | 0 | 530.3057 |  |  | 551.7718
| 40626.5868 | 60.036 | 547.5976 |  |  | 550 | -3.5031 | -4.6435 | 0.086398 |  | 0 | 530.4761 |  |  | 551.7718
| 40626.5869 | 60.033 | 546.1004 |  |  | 550 | -2.9502 | -4.4234 | 0.079202 |  | 0 | 530.6962 |  |  | 551.7718
| 40626.5869 | 60.031 | 546.1004 |  |  | 550 | -2.581 | -4.1839 | 0.074396 |  | 0 | 530.9358 |  |  | 551.7718
| 40626.5869 | 60.035 | 545.7265 |  |  | 550 | -3.3188 | -4.0714 | 0.084 |  | 0 | 531.0482 |  |  | 551.7718
| 40626.5869 | 60.037 | 545.7265 |  |  | 550 | -3.6873 | -4.0215 | 0.088797 |  | 0 | 531.0981 |  |  | 551.7718
| 40626.5869 | 60.04 | 545.4362 |  |  | 550 | -4.2409 | -4.05 | 0.096002 |  | 0 | 531.0696 |  |  | 551.7718
| 40626.587 | 60.039 | 545.4362 |  |  | 550 | -4.0566 | -4.0509 | 0.093604 |  | 0 | 531.0688 |  |  | 551.7718
| 40626.587 | 60.038 | 545.7387 |  |  | 550 | -3.8716 | -4.0276 | 0.091196 |  | 0 | 531.0921 |  |  | 551.7718
| 40626.587 | 60.036 | 545.7387 |  |  | 550 | -3.5031 | -3.9594 | 0.086398 |  | 0 | 531.1603 |  |  | 551.7718
| 40626.587 | 60.032 | 545.1893 |  |  | 550 | -2.7659 | -3.8042 | 0.076804 |  | 0 | 531.3154 |  |  | 551.7718
| 40626.5871 | 60.03 | 545.1893 |  |  | 550 | -2.3967 | -3.6212 | 0.071997 |  | 0 | 531.4984 |  |  | 551.7718
| 40626.5871 | 60.03 | 546.3142 |  |  | 550 | -2.3967 | -3.4621 | 0.071997 |  | 0 | 531.6576 |  |  | 551.7718
| 40626.5871 | 60.029 | 546.3142 |  |  | 550 | -2.2124 | -3.2996 | 0.069598 |  | 0 | 531.82 |  |  | 551.7718
| 40626.5871 | 60.032 | 545.6485 |  |  | 550 | -2.7659 | -3.2302 | 0.076804 |  | 0 | 531.8894 |  |  | 551.7718
| 40626.5872 | 60.032 | 545.6485 |  |  | 550 | -2.7659 | -3.1699 | 0.076804 |  | 0 | 531.9498 |  |  | 551.7718
| 40626.5872 | 60.03 | 545.5865 |  |  | 550 | -2.3967 | -3.0694 | 0.071997 |  | 0 | 532.0503 |  |  | 551.7718
| 40626.5872 | 60.032 | 545.5865 |  |  | 550 | -2.7659 | -3.0299 | 0.076804 |  | 0 | 532.0897 |  |  | 551.7718
| 40626.5872 | 60.029 | 543.9636 |  |  | 550 | -2.2124 | -2.9236 | 0.069598 |  | 0 | 532.196 |  |  | 551.7718
| 40626.5872 | 60.026 | 543.9636 |  |  | 550 | -1.6596 | -2.7593 | 0.062402 |  | 0 | 532.3603 |  |  | 551.7718
| 40626.5873 | 60.025 | 543.4549 |  |  | 550 | -1.4753 | -2.5924 | 0.060004 |  | 0 | 532.5272 |  |  | 551.7718
| 40626.5873 | 60.02 | 543.4549 |  |  | 550 | -0.55322 | -2.3273 | 0.048001 |  | 0 | 532.7923 |  |  | 551.7718
| 40626.5873 | 60.023 | 542.8652 |  |  | 550 | -1.106 | -2.1685 | 0.055197 |  | 0 | 532.9511 |  |  | 551.7718
| 40626.5873 | 60.016 | 542.8652 |  |  | 550 | 0 | -1.8866 | 0.038397 |  | 0 | 533.233 |  |  | 551.7718
| 40626.5874 | 60.012 | 543.6949 |  |  | 550 | 0 | -1.6414 | 0.028802 |  | 0 | 533.4783 |  |  | 551.7718
| 40626.5874 | 60.011 | 543.6949 |  |  | 550 | 0 | -1.428 | 0.026404 |  | 0 | 533.6916 |  |  | 551.7718
| 40626.5874 | 60.01 | 543.2955 |  |  | 550 | 0 | -1.2423 | 0.023996 |  | 0 | 533.8773 |  |  | 551.7718
| 40626.5874 | 60.008 | 543.2955 |  |  | 550 | 0 | -1.0808 | 0.019199 |  | 0 | 534.0388 |  |  | 551.7718
| 40626.5875 | 60.01 | 543.6184 |  |  | 550 | 0 | -0.94033 | 0.023996 |  | 0 | 534.1793 |  |  | 551.7718
| 40626.5875 | 60.011 | 543.8499 |  |  | 550 | 0 | -0.81809 | 0.026404 |  | 0 | 534.3015 |  |  | 551.7718
| 40626.5875 | 60.012 | 543.8499 |  |  | 550 | 0 | -0.71174 | 0.028802 |  | 0 | 534.4079 |  |  | 551.7718
| 40626.5875 | 60.014 | 543.8499 |  |  | 550 | 0 | -0.61921 | 0.0336 |  | 0 | 534.5004 |  |  | 551.7718
| 40626.5875 | 60.016 | 543.7864 |  |  | 550 | 0 | -0.53872 | 0.038397 |  | 0 | 534.5809 |  |  | 551.7718
| 40626.5876 | 60.018 | 543.7864 |  |  | 550 | -0.18467 | -0.49269 | 0.043204 |  | 0 | 534.6269 |  |  | 551.7718
| 40626.5876 | 60.018 | 543.9342 |  |  | 550 | -0.18467 | -0.45265 | 0.043204 |  | 0 | 534.667 |  |  | 551.7718
| 40626.5876 | 60.02 | 543.9342 |  |  | 550 | -0.55322 | -0.46572 | 0.048001 |  | 0 | 534.6539 |  |  | 551.7718
| 40626.5876 | 60.018 | 544.7661 |  |  | 550 | -0.18467 | -0.42918 | 0.043204 |  | 0 | 534.6905 |  |  | 551.7718
| 40626.5877 | 60.017 | 544.7661 |  |  | 550 | 0 | -0.37339 | 0.040796 |  | 0 | 534.7462 |  |  | 551.7718
| 40626.5877 | 60.017 | 544.2815 |  |  | 550 | 0 | -0.32485 | 0.040796 |  | 0 | 534.7948 |  |  | 551.7718
| 40626.5877 | 60.017 | 544.998 |  |  | 550 | 0 | -0.28262 | 0.040796 |  | 0 | 534.837 |  |  | 551.7718
| 40626.5877 | 60.016 | 544.998 |  |  | 550 | 0 | -0.24588 | 0.038397 |  | 0 | 534.8738 |  |  | 551.7718
| 40626.5878 | 60.018 | 544.998 |  |  | 550 | -0.18467 | -0.23792 | 0.043204 |  | 0 | 534.8817 |  |  | 551.7718
| 40626.5878 | 60.022 | 544.2836 |  |  | 550 | -0.92177 | -0.32682 | 0.052798 |  | 0 | 534.7928 |  |  | 551.7718
| 40626.5878 | 60.023 | 544.2836 |  |  | 550 | -1.106 | -0.42812 | 0.055197 |  | 0 | 534.6915 |  |  | 551.7718
| 40626.5878 | 60.022 | 543.6278 |  |  | 550 | -0.92177 | -0.4923 | 0.052798 |  | 0 | 534.6273 |  |  | 551.7718
| 40626.5878 | 60.033 | 543.6278 |  |  | 550 | -2.9502 | -0.81183 | 0.079202 |  | 0 | 534.3078 |  |  | 551.7718
| 40626.5879 | 60.042 | 542.7296 |  |  | 550 | -4.6094 | -1.3055 | 0.1008 |  | 0 | 533.8141 |  |  | 551.7718
| 40626.5879 | 60.052 | 542.7296 |  |  | 550 | -6.4529 | -1.9747 | 0.1248 |  | 0 | 533.145 |  |  | 551.7718
| 40626.5879 | 60.048 | 541.7638 |  |  | 550 | -5.7158 | -2.461 | 0.1152 |  | 0 | 532.6586 |  |  | 551.7718
| 40626.5879 | 60.044 | 541.7638 |  |  | 550 | -4.978 | -2.7882 | 0.1056 |  | 0 | 532.3314 |  |  | 551.7718
| 40626.588 | 60.042 | 540.6999 |  |  | 550 | -4.6094 | -3.025 | 0.1008 |  | 0 | 532.0947 |  |  | 551.7718
| 40626.588 | 60.041 | 540.6999 |  |  | 550 | -4.4251 | -3.207 | 0.098401 |  | 0 | 531.9126 |  |  | 551.7718
| 40626.588 | 60.044 | 540.5129 |  |  | 550 | -4.978 | -3.4372 | 0.1056 |  | 0 | 531.6824 |  |  | 551.7718
| 40626.588 | 60.042 | 540.5129 |  |  | 550 | -4.6094 | -3.5896 | 0.1008 |  | 0 | 531.53 |  |  | 551.7718
| 40626.5881 | 60.042 | 541.0801 |  |  | 550 | -4.6094 | -3.7222 | 0.1008 |  | 0 | 531.3975 |  |  | 551.7718
| 40626.5881 | 60.041 | 541.0801 |  |  | 550 | -4.4251 | -3.8136 | 0.098401 |  | 0 | 531.3061 |  |  | 551.7718
| 40626.5881 | 60.038 | 540.7869 |  |  | 550 | -3.8716 | -3.8211 | 0.091196 |  | 0 | 531.2985 |  |  | 551.7718
| 40626.5881 | 60.037 | 540.7869 |  |  | 550 | -3.6873 | -3.8037 | 0.088797 |  | 0 | 531.3159 |  |  | 551.7718
| 40626.5881 | 60.036 | 541.9575 |  |  | 550 | -3.5031 | -3.7646 | 0.086398 |  | 0 | 531.355 |  |  | 551.7718
| 40626.5882 | 60.041 | 541.9575 |  |  | 550 | -4.4251 | -3.8505 | 0.098401 |  | 0 | 531.2691 |  |  | 551.7718
| 40626.5882 | 60.036 | 540.6132 |  |  | 550 | -3.5031 | -3.8053 | 0.086398 |  | 0 | 531.3143 |  |  | 551.7718
| 40626.5882 | 60.037 | 540.6132 |  |  | 550 | -3.6873 | -3.79 | 0.088797 |  | 0 | 531.3296 |  |  | 551.7718
| 40626.5882 | 60.037 | 540.6246 |  |  | 550 | -3.6873 | -3.7766 | 0.088797 |  | 0 | 531.343 |  |  | 551.7718
| 40626.5883 | 60.036 | 540.6246 |  |  | 550 | -3.5031 | -3.7411 | 0.086398 |  | 0 | 531.3786 |  |  | 551.7718
| 40626.5883 | 60.035 | 541.1522 |  |  | 550 | -3.3188 | -3.6862 | 0.084 |  | 0 | 531.4335 |  |  | 551.7718
| 40626.5883 | 60.034 | 541.1522 |  |  | 550 | -3.1345 | -3.6145 | 0.081601 |  | 0 | 531.5052 |  |  | 551.7718
| 40626.5883 | 60.032 | 540.2507 |  |  | 550 | -2.7659 | -3.5042 | 0.076804 |  | 0 | 531.6155 |  |  | 551.7718
| 40626.5884 | 60.035 | 540.2507 |  |  | 550 | -3.3188 | -3.4801 | 0.084 |  | 0 | 531.6396 |  |  | 551.7718
| 40626.5884 | 60.037 | 539.8033 |  |  | 550 | -3.6873 | -3.507 | 0.088797 |  | 0 | 531.6126 |  |  | 551.7718
| 40626.5884 | 60.037 | 539.8033 |  |  | 550 | -3.6873 | -3.5304 | 0.088797 |  | 0 | 531.5892 |  |  | 551.7718
| 40626.5884 | 60.035 | 539.3864 |  |  | 550 | -3.3188 | -3.5029 | 0.084 |  | 0 | 531.6167 |  |  | 551.7718
| 40626.5884 | 60.035 | 539.3864 |  |  | 550 | -3.3188 | -3.479 | 0.084 |  | 0 | 531.6406 |  |  | 551.7718
| 40626.5885 | 60.032 | 539.1969 |  |  | 550 | -2.7659 | -3.3863 | 0.076804 |  | 0 | 531.7333 |  |  | 551.7718
| 40626.5885 | 60.037 | 539.1969 |  |  | 550 | -3.6873 | -3.4254 | 0.088797 |  | 0 | 531.6942 |  |  | 551.7718
| 40626.5885 | 60.036 | 539.8394 |  |  | 550 | -3.5031 | -3.4355 | 0.086398 |  | 0 | 531.6841 |  |  | 551.7718
| 40626.5885 | 60.041 | 539.8394 |  |  | 550 | -4.4251 | -3.5642 | 0.098401 |  | 0 | 531.5555 |  |  | 551.7718
| 40626.5886 | 60.04 | 539.6266 |  |  | 550 | -4.2409 | -3.6521 | 0.096002 |  | 0 | 531.4675 |  |  | 551.7718
| 40626.5886 | 60.038 | 539.6266 |  |  | 550 | -3.8716 | -3.6807 | 0.091196 |  | 0 | 531.439 |  |  | 551.7718
| 40626.5886 | 60.037 | 540.0292 |  |  | 550 | -3.6873 | -3.6815 | 0.088797 |  | 0 | 531.4381 |  |  | 551.7718
| 40626.5886 | 60.04 | 540.0292 |  |  | 550 | -4.2409 | -3.7543 | 0.096002 |  | 0 | 531.3654 |  |  | 551.7718
| 40626.5887 | 60.039 | 537.6292 |  |  | 550 | -4.0566 | -3.7936 | 0.093604 |  | 0 | 531.3261 |  |  | 551.7718
| 40626.5887 | 60.036 | 537.6292 |  |  | 550 | -3.5031 | -3.7558 | 0.086398 |  | 0 | 531.3638 |  |  | 551.7718
| 40626.5887 | 60.039 | 538.2805 |  |  | 550 | -4.0566 | -3.7949 | 0.093604 |  | 0 | 531.3247 |  |  | 551.7718
| 40626.5887 | 60.037 | 538.2805 |  |  | 550 | -3.6873 | -3.7809 | 0.088797 |  | 0 | 531.3387 |  |  | 551.7718
| 40626.5887 | 60.035 | 539.3442 |  |  | 550 | -3.3188 | -3.7208 | 0.084 |  | 0 | 531.3988 |  |  | 551.7718
| 40626.5888 | 60.032 | 539.3442 |  |  | 550 | -2.7659 | -3.5967 | 0.076804 |  | 0 | 531.5229 |  |  | 551.7718
| 40626.5888 | 60.033 | 539.9172 |  |  | 550 | -2.9502 | -3.5127 | 0.079202 |  | 0 | 531.607 |  |  | 551.7718
| 40626.5888 | 60.035 | 539.9172 |  |  | 550 | -3.3188 | -3.4875 | 0.084 |  | 0 | 531.6322 |  |  | 551.7718
| 40626.5888 | 60.034 | 539.979 |  |  | 550 | -3.1345 | -3.4416 | 0.081601 |  | 0 | 531.6781 |  |  | 551.7718
| 40626.5889 | 60.033 | 539.979 |  |  | 550 | -2.9502 | -3.3777 | 0.079202 |  | 0 | 531.7419 |  |  | 551.7718
| 40626.5889 | 60.036 | 539.7486 |  |  | 550 | -3.5031 | -3.394 | 0.086398 |  | 0 | 531.7256 |  |  | 551.7718
| 40626.5889 | 60.033 | 539.7486 |  |  | 550 | -2.9502 | -3.3363 | 0.079202 |  | 0 | 531.7833 |  |  | 551.7718
| 40626.5889 | 60.033 | 540.1162 |  |  | 550 | -2.9502 | -3.2861 | 0.079202 |  | 0 | 531.8335 |  |  | 551.7718
| 40626.589 | 60.032 | 540.1162 |  |  | 550 | -2.7659 | -3.2185 | 0.076804 |  | 0 | 531.9011 |  |  | 551.7718
| 40626.589 | 60.027 | 540.6266 |  |  | 550 | -1.8439 | -3.0398 | 0.064801 |  | 0 | 532.0798 |  |  | 551.7718
| 40626.589 | 60.025 | 540.6266 |  |  | 550 | -1.4753 | -2.8364 | 0.060004 |  | 0 | 532.2832 |  |  | 551.7718
| 40626.589 | 60.025 | 540.9314 |  |  | 550 | -1.4753 | -2.6595 | 0.060004 |  | 0 | 532.4602 |  |  | 551.7718
| 40626.5891 | 60.014 | 540.9314 |  |  | 550 | 0 | -2.3137 | 0.0336 |  | 0 | 532.8059 |  |  | 551.7718
| 40626.5891 | 60.014 | 541.9986 |  |  | 550 | 0 | -2.0129 | 0.0336 |  | 0 | 533.1067 |  |  | 551.7718
| 40626.5891 | 60.005 | 541.9986 |  |  | 550 | 0 | -1.7513 | 0.012003 |  | 0 | 533.3684 |  |  | 551.7718
| 40626.5891 | 60 | 541.3756 |  |  | 550 | 0 | -1.5236 | 0 |  | 0 | 533.596 |  |  | 551.7718
| 40626.5891 | 59.994 | 541.3756 |  |  | 550 | 0 | -1.3255 | -0.014401 |  | 0 | 533.7941 |  |  | 551.7718
| 40626.5892 | 59.977 | 543.6105 |  |  | 550 | 1.106 | -1.0094 | -0.055197 |  | 0 | 534.1102 |  |  | 551.7718
| 40626.5892 | 59.973 | 543.6105 |  |  | 550 | 1.8439 | -0.6385 | -0.064801 |  | 0 | 534.4811 |  |  | 551.7718
| 40626.5892 | 59.97 | 544.2067 |  |  | 550 | 2.3967 | -0.24392 | -0.071997 |  | 0 | 534.8757 |  |  | 551.7718
| 40626.5892 | 59.97 | 544.2067 |  |  | 550 | 2.3967 | 0.099356 | -0.071997 |  | 0 | 535.219 |  |  | 551.7718
| 40626.5893 | 59.968 | 545.4058 |  |  | 550 | 2.7659 | 0.44601 | -0.076804 |  | 0 | 535.5656 |  |  | 551.7718
| 40626.5893 | 59.969 | 545.4058 |  |  | 550 | 2.581 | 0.72356 | -0.074396 |  | 0 | 535.8432 |  |  | 551.7718
| 40626.5893 | 59.969 | 547.0699 |  |  | 550 | 2.581 | 0.96502 | -0.074396 |  | 0 | 536.0847 |  |  | 551.7718
| 40626.5893 | 59.965 | 547.0699 |  |  | 550 | 3.3188 | 1.271 | -0.084 |  | 0 | 536.3906 |  |  | 551.7718
| 40626.5894 | 59.964 | 547.2808 |  |  | 550 | 3.5031 | 1.5612 | -0.086398 |  | 0 | 536.6808 |  |  | 551.7718
| 40626.5894 | 59.964 | 547.2808 |  |  | 550 | 3.5031 | 1.8136 | -0.086398 |  | 0 | 536.9333 |  |  | 551.7718
| 40626.5894 | 59.97 | 549.0167 |  |  | 550 | 2.3967 | 1.8894 | -0.071997 |  | 0 | 537.0091 |  |  | 551.7718
| 40626.5894 | 59.969 | 549.0167 |  |  | 550 | 2.581 | 1.9793 | -0.074396 |  | 0 | 537.099 |  |  | 551.7718
| 40626.5894 | 59.971 | 551.0373 |  |  | 550 | 2.2124 | 2.0096 | -0.069598 |  | 0 | 537.1293 |  |  | 551.7718
| 40626.5895 | 59.974 | 551.0373 |  |  | 550 | 1.6596 | 1.9641 | -0.062402 |  | 0 | 537.0838 |  |  | 551.7718
| 40626.5895 | 59.975 | 551.6588 |  |  | 550 | 1.4753 | 1.9006 | -0.060004 |  | 0 | 537.0202 |  |  | 551.7718
| 40626.5895 | 59.976 | 551.6588 |  |  | 550 | 1.2903 | 1.8212 | -0.057596 |  | 0 | 536.9409 |  |  | 551.7718
| 40626.5895 | 59.977 | 551.348 |  |  | 550 | 1.106 | 1.7283 | -0.055197 |  | 0 | 536.8479 |  |  | 551.7718
| 40626.5896 | 59.977 | 551.348 |  |  | 550 | 1.106 | 1.6474 | -0.055197 |  | 0 | 536.767 |  |  | 551.7718
| 40626.5896 | 59.976 | 550.2926 |  |  | 550 | 1.2903 | 1.601 | -0.057596 |  | 0 | 536.7206 |  |  | 551.7718
| 40626.5896 | 59.973 | 550.2926 |  |  | 550 | 1.8439 | 1.6325 | -0.064801 |  | 0 | 536.7522 |  |  | 551.7718
| 40626.5896 | 59.975 | 551.9522 |  |  | 550 | 1.4753 | 1.6121 | -0.060004 |  | 0 | 536.7317 |  |  | 551.7718
| 40626.5897 | 59.977 | 551.9522 |  |  | 550 | 1.106 | 1.5463 | -0.055197 |  | 0 | 536.6659 |  |  | 551.7718
| 40626.5897 | 59.973 | 552.2561 |  |  | 550 | 1.8439 | 1.585 | -0.064801 |  | 0 | 536.7046 |  |  | 551.7718
| 40626.5897 | 59.969 | 552.2561 |  |  | 550 | 2.581 | 1.7145 | -0.074396 |  | 0 | 536.8341 |  |  | 551.7718
| 40626.5897 | 59.966 | 552.5391 |  |  | 550 | 3.1345 | 1.8991 | -0.081601 |  | 0 | 537.0187 |  |  | 551.7718
| 40626.5897 | 59.966 | 552.5391 |  |  | 550 | 3.1345 | 2.0597 | -0.081601 |  | 0 | 537.1793 |  |  | 551.7718
| 40626.5898 | 59.965 | 552.8584 |  |  | 550 | 3.3188 | 2.2234 | -0.084 |  | 0 | 537.343 |  |  | 551.7718
| 40626.5898 | 59.965 | 552.8584 |  |  | 550 | 3.3188 | 2.3658 | -0.084 |  | 0 | 537.4854 |  |  | 551.7718
| 40626.5898 | 59.968 | 554.4174 |  |  | 550 | 2.7659 | 2.4178 | -0.076804 |  | 0 | 537.5374 |  |  | 551.7718
| 40626.5898 | 59.964 | 554.4174 |  |  | 550 | 3.5031 | 2.5589 | -0.086398 |  | 0 | 537.6785 |  |  | 551.7718
| 40626.5899 | 59.964 | 554.3207 |  |  | 550 | 3.5031 | 2.6816 | -0.086398 |  | 0 | 537.8013 |  |  | 551.7718
| 40626.5899 | 59.966 | 554.3207 |  |  | 550 | 3.1345 | 2.7405 | -0.081601 |  | 0 | 537.8601 |  |  | 551.7718
| 40626.5899 | 59.971 | 553.5225 |  |  | 550 | 2.2124 | 2.6718 | -0.069598 |  | 0 | 537.7915 |  |  | 551.7718
| 40626.5899 | 59.973 | 553.5225 |  |  | 550 | 1.8439 | 2.5642 | -0.064801 |  | 0 | 537.6838 |  |  | 551.7718
| 40626.59 | 59.975 | 553.7564 |  |  | 550 | 1.4753 | 2.4226 | -0.060004 |  | 0 | 537.5423 |  |  | 551.7718
| 40626.59 | 59.979 | 553.7564 |  |  | 550 | 0.7375 | 2.2036 | -0.0504 |  | 0 | 537.3232 |  |  | 551.7718
| 40626.59 | 59.981 | 552.7703 |  |  | 550 | 0.36894 | 1.9651 | -0.045602 |  | 0 | 537.0847 |  |  | 551.7718
| 40626.59 | 59.983 | 552.7703 |  |  | 550 | 0 | 1.7096 | -0.040796 |  | 0 | 536.8293 |  |  | 551.7718
| 40626.59 | 59.98 | 554.7769 |  |  | 550 | 0.55322 | 1.5593 | -0.048001 |  | 0 | 536.6789 |  |  | 551.7718
| 40626.5901 | 59.979 | 554.7769 |  |  | 550 | 0.7375 | 1.4525 | -0.0504 |  | 0 | 536.5721 |  |  | 551.7718
| 40626.5901 | 59.982 | 555.6833 |  |  | 550 | 0.18467 | 1.2876 | -0.043204 |  | 0 | 536.4073 |  |  | 551.7718
| 40626.5901 | 59.987 | 555.6833 |  |  | 550 | 0 | 1.1202 | -0.031201 |  | 0 | 536.2399 |  |  | 551.7718
| 40626.5901 | 59.994 | 554.7871 |  |  | 550 | 0 | 0.97461 | -0.014401 |  | 0 | 536.0943 |  |  | 551.7718
| 40626.5902 | 59.998 | 554.7871 |  |  | 550 | 0 | 0.84791 | -0.0047974 |  | 0 | 535.9676 |  |  | 551.7718
| 40626.5902 | 59.997 | 556.4283 |  |  | 550 | 0 | 0.73769 | -0.007196 |  | 0 | 535.8573 |  |  | 551.7718
| 40626.5902 | 59.996 | 556.4283 |  |  | 550 | 0 | 0.64179 | -0.0096039 |  | 0 | 535.7614 |  |  | 551.7718
| 40626.5902 | 59.996 | 554.0075 |  |  | 550 | 0 | 0.55835 | -0.0096039 |  | 0 | 535.678 |  |  | 551.7718
| 40626.5903 | 59.994 | 554.0075 |  |  | 550 | 0 | 0.48577 | -0.014401 |  | 0 | 535.6054 |  |  | 551.7718
| 40626.5903 | 59.991 | 553.3033 |  |  | 550 | 0 | 0.42262 | -0.021597 |  | 0 | 535.5423 |  |  | 551.7718
| 40626.5903 | 59.987 | 553.3033 |  |  | 550 | 0 | 0.36768 | -0.031201 |  | 0 | 535.4873 |  |  | 551.7718
| 40626.5903 | 59.987 | 553.3033 |  |  | 550 | 0 | 0.31988 | -0.031201 |  | 0 | 535.4395 |  |  | 551.7718
| 40626.5903 | 59.986 | 553.9601 |  |  | 550 | 0 | 0.2783 | -0.0336 |  | 0 | 535.3979 |  |  | 551.7718
| 40626.5904 | 59.996 | 553.9601 |  |  | 550 | 0 | 0.24212 | -0.0096039 |  | 0 | 535.3618 |  |  | 551.7718
| 40626.5904 | 59.999 | 553.348 |  |  | 550 | 0 | 0.21064 | -0.0023987 |  | 0 | 535.3303 |  |  | 551.7718
| 40626.5904 | 60.001 | 553.348 |  |  | 550 | 0 | 0.18326 | 0.0023987 |  | 0 | 535.3029 |  |  | 551.7718
| 40626.5904 | 60.008 | 552.6059 |  |  | 550 | 0 | 0.15943 | 0.019199 |  | 0 | 535.2791 |  |  | 551.7718
| 40626.5905 | 60.012 | 552.6059 |  |  | 550 | 0 | 0.13871 | 0.028802 |  | 0 | 535.2583 |  |  | 551.7718
| 40626.5905 | 60.013 | 552.3778 |  |  | 550 | 0 | 0.12068 | 0.031201 |  | 0 | 535.2403 |  |  | 551.7718
| 40626.5905 | 60.014 | 552.3778 |  |  | 550 | 0 | 0.10499 | 0.0336 |  | 0 | 535.2246 |  |  | 551.7718
| 40626.5905 | 60.013 | 552.1105 |  |  | 550 | 0 | 0.09134 | 0.031201 |  | 0 | 535.211 |  |  | 551.7718
| 40626.5906 | 60.014 | 552.1105 |  |  | 550 | 0 | 0.079466 | 0.0336 |  | 0 | 535.1991 |  |  | 551.7718
| 40626.5906 | 60.011 | 553.2075 |  |  | 550 | 0 | 0.069135 | 0.026404 |  | 0 | 535.1888 |  |  | 551.7718
| 40626.5906 | 60.011 | 553.2075 |  |  | 550 | 0 | 0.060148 | 0.026404 |  | 0 | 535.1798 |  |  | 551.7718
| 40626.5906 | 60.007 | 553.1398 |  |  | 550 | 0 | 0.052328 | 0.0168 |  | 0 | 535.172 |  |  | 551.7718
| 40626.5906 | 60.006 | 553.1398 |  |  | 550 | 0 | 0.045526 | 0.014401 |  | 0 | 535.1652 |  |  | 551.7718
| 40626.5907 | 60.005 | 553.2218 |  |  | 550 | 0 | 0.039607 | 0.012003 |  | 0 | 535.1592 |  |  | 551.7718
| 40626.5907 | 60.004 | 553.2218 |  |  | 550 | 0 | 0.034458 | 0.0096039 |  | 0 | 535.1541 |  |  | 551.7718
| 40626.5907 | 60.004 | 553.2479 |  |  | 550 | 0 | 0.029979 | 0.0096039 |  | 0 | 535.1496 |  |  | 551.7718
| 40626.5907 | 60.003 | 553.2479 |  |  | 550 | 0 | 0.026082 | 0.007196 |  | 0 | 535.1457 |  |  | 551.7718
| 40626.5908 | 60.005 | 552.1477 |  |  | 550 | 0 | 0.022691 | 0.012003 |  | 0 | 535.1423 |  |  | 551.7718
| 40626.5908 | 60.005 | 552.1477 |  |  | 550 | 0 | 0.019741 | 0.012003 |  | 0 | 535.1394 |  |  | 551.7718
| 40626.5908 | 60.006 | 552.4413 |  |  | 550 | 0 | 0.017175 | 0.014401 |  | 0 | 535.1368 |  |  | 551.7718
| 40626.5908 | 60.005 | 552.4413 |  |  | 550 | 0 | 0.014942 | 0.012003 |  | 0 | 535.1346 |  |  | 551.7718
| 40626.5909 | 60.003 | 552.2262 |  |  | 550 | 0 | 0.013 | 0.007196 |  | 0 | 535.1326 |  |  | 551.7718
| 40626.5909 | 60.004 | 552.2262 |  |  | 550 | 0 | 0.01131 | 0.0096039 |  | 0 | 535.1309 |  |  | 551.7718
| 40626.5909 | 60.002 | 552.241 |  |  | 550 | 0 | 0.0098394 | 0.0047974 |  | 0 | 535.1295 |  |  | 551.7718
| 40626.5909 | 60.001 | 552.241 |  |  | 550 | 0 | 0.0085603 | 0.0023987 |  | 0 | 535.1282 |  |  | 551.7718
| 40626.5909 | 59.998 | 550.9891 |  |  | 550 | 0 | 0.0074474 | -0.0047974 |  | 0 | 535.1271 |  |  | 551.7718
| 40626.591 | 59.997 | 550.9891 |  |  | 550 | 0 | 0.0064793 | -0.007196 |  | 0 | 535.1261 |  |  | 551.7718
| 40626.591 | 59.997 | 551.2598 |  |  | 550 | 0 | 0.005637 | -0.007196 |  | 0 | 535.1253 |  |  | 551.7718
| 40626.591 | 59.995 | 551.2598 |  |  | 550 | 0 | 0.0049042 | -0.012003 |  | 0 | 535.1245 |  |  | 551.7718
| 40626.591 | 59.994 | 550.8966 |  |  | 550 | 0 | 0.0042666 | -0.014401 |  | 0 | 535.1239 |  |  | 551.7718
| 40626.5911 | 59.991 | 550.8966 |  |  | 550 | 0 | 0.003712 | -0.021597 |  | 0 | 535.1233 |  |  | 551.7718
| 40626.5911 | 59.993 | 551.3008 |  |  | 550 | 0 | 0.0032294 | -0.0168 |  | 0 | 535.1229 |  |  | 551.7718
| 40626.5911 | 59.993 | 551.3008 |  |  | 550 | 0 | 0.0028096 | -0.0168 |  | 0 | 535.1224 |  |  | 551.7718
| 40626.5911 | 59.99 | 551.201 |  |  | 550 | 0 | 0.0024443 | -0.023996 |  | 0 | 535.1221 |  |  | 551.7718
| 40626.5912 | 59.99 | 551.201 |  |  | 550 | 0 | 0.0021266 | -0.023996 |  | 0 | 535.1218 |  |  | 551.7718
| 40626.5912 | 59.988 | 551.0599 |  |  | 550 | 0 | 0.0018501 | -0.028802 |  | 0 | 535.1215 |  |  | 551.7718
| 40626.5912 | 59.988 | 551.0599 |  |  | 550 | 0 | 0.0016096 | -0.028802 |  | 0 | 535.1212 |  |  | 551.7718
| 40626.5912 | 59.99 | 551.7879 |  |  | 550 | 0 | 0.0014004 | -0.023996 |  | 0 | 535.121 |  |  | 551.7718
| 40626.5912 | 59.993 | 551.7879 |  |  | 550 | 0 | 0.0012183 | -0.0168 |  | 0 | 535.1209 |  |  | 551.7718
| 40626.5913 | 59.995 | 551.0947 |  |  | 550 | 0 | 0.0010599 | -0.012003 |  | 0 | 535.1207 |  |  | 551.7718
| 40626.5913 | 59.997 | 551.0947 |  |  | 550 | 0 | 0.00092214 | -0.007196 |  | 0 | 535.1206 |  |  | 551.7718
| 40626.5913 | 59.997 | 550.8473 |  |  | 550 | 0 | 0.00080226 | -0.007196 |  | 0 | 535.1204 |  |  | 551.7718
| 40626.5913 | 59.996 | 550.8473 |  |  | 550 | 0 | 0.00069797 | -0.0096039 |  | 0 | 535.1203 |  |  | 551.7718
| 40626.5914 | 59.993 | 551.1833 |  |  | 550 | 0 | 0.00060723 | -0.0168 |  | 0 | 535.1202 |  |  | 551.7718
| 40626.5914 | 59.993 | 551.1833 |  |  | 550 | 0 | 0.00052829 | -0.0168 |  | 0 | 535.1202 |  |  | 551.7718
| 40626.5914 | 59.99 | 551.02 |  |  | 550 | 0 | 0.00045961 | -0.023996 |  | 0 | 535.1201 |  |  | 551.7718
| 40626.5914 | 59.994 | 551.02 |  |  | 550 | 0 | 0.00039986 | -0.014401 |  | 0 | 535.12 |  |  | 551.7718
| 40626.5915 | 59.992 | 549.6554 |  |  | 550 | 0 | 0.00034788 | -0.019199 |  | 0 | 535.12 |  |  | 551.7718
| 40626.5915 | 59.987 | 549.6554 |  |  | 550 | 0 | 0.00030266 | -0.031201 |  | 0 | 535.1199 |  |  | 551.7718
| 40626.5915 | 59.984 | 549.2314 |  |  | 550 | 0 | 0.00026331 | -0.038397 |  | 0 | 535.1199 |  |  | 551.7718
| 40626.5915 | 59.984 | 549.2314 |  |  | 550 | 0 | 0.00022908 | -0.038397 |  | 0 | 535.1199 |  |  | 551.7718
| 40626.5916 | 59.983 | 549.9525 |  |  | 550 | 0 | 0.0001993 | -0.040796 |  | 0 | 535.1198 |  |  | 551.7718
| 40626.5916 | 59.986 | 549.9525 |  |  | 550 | 0 | 0.00017339 | -0.0336 |  | 0 | 535.1198 |  |  | 551.7718
| 40626.5916 | 59.986 | 548.9944 |  |  | 550 | 0 | 0.00015085 | -0.0336 |  | 0 | 535.1198 |  |  | 551.7718
| 40626.5916 | 59.986 | 548.9944 |  |  | 550 | 0 | 0.00013124 | -0.0336 |  | 0 | 535.1198 |  |  | 551.7718
| 40626.5916 | 59.986 | 549.8294 |  |  | 550 | 0 | 0.00011418 | -0.0336 |  | 0 | 535.1198 |  |  | 551.7718
| 40626.5917 | 59.988 | 549.8294 |  |  | 550 | 0 | 9.9335e-05 | -0.028802 |  | 0 | 535.1197 |  |  | 551.7718
| 40626.5917 | 59.991 | 549.9199 |  |  | 550 | 0 | 8.6422e-05 | -0.021597 |  | 0 | 535.1197 |  |  | 551.7718
| 40626.5917 | 59.991 | 549.9199 |  |  | 550 | 0 | 7.5187e-05 | -0.021597 |  | 0 | 535.1197 |  |  | 551.7718
| 40626.5917 | 59.993 | 549.7203 |  |  | 550 | 0 | 6.5413e-05 | -0.0168 |  | 0 | 535.1197 |  |  | 551.7718
| 40626.5918 | 59.992 | 549.7203 |  |  | 550 | 0 | 5.6909e-05 | -0.019199 |  | 0 | 535.1197 |  |  | 551.7718
| 40626.5918 | 59.99 | 549.6021 |  |  | 550 | 0 | 4.9511e-05 | -0.023996 |  | 0 | 535.1197 |  |  | 551.7718
| 40626.5918 | 59.985 | 549.6021 |  |  | 550 | 0 | 4.3074e-05 | -0.035999 |  | 0 | 535.1197 |  |  | 551.7718
| 40626.5918 | 59.984 | 551.3003 |  |  | 550 | 0 | 3.7475e-05 | -0.038397 |  | 0 | 535.1197 |  |  | 551.7718
| 40626.5919 | 59.984 | 551.3003 |  |  | 550 | 0 | 3.2603e-05 | -0.038397 |  | 0 | 535.1197 |  |  | 551.7718
| 40626.5919 | 59.98 | 551.7938 |  |  | 550 | 0.55322 | 0.071947 | -0.048001 |  | 0 | 535.1916 |  |  | 551.7718
| 40626.5919 | 59.978 | 551.7938 |  |  | 550 | 0.92177 | 0.18242 | -0.052798 |  | 0 | 535.3021 |  |  | 551.7718
| 40626.5919 | 59.977 | 550.3602 |  |  | 550 | 1.106 | 0.3025 | -0.055197 |  | 0 | 535.4221 |  |  | 551.7718
| 40626.5919 | 59.979 | 550.3602 |  |  | 550 | 0.7375 | 0.35905 | -0.0504 |  | 0 | 535.4787 |  |  | 551.7718
| 40626.592 | 59.976 | 551.4059 |  |  | 550 | 1.2903 | 0.48011 | -0.057596 |  | 0 | 535.5997 |  |  | 551.7718
| 40626.592 | 59.971 | 551.4059 |  |  | 550 | 2.2124 | 0.70531 | -0.069598 |  | 0 | 535.8249 |  |  | 551.7718
| 40626.592 | 59.971 | 550.7222 |  |  | 550 | 2.2124 | 0.90123 | -0.069598 |  | 0 | 536.0209 |  |  | 551.7718
| 40626.592 | 59.974 | 550.7222 |  |  | 550 | 1.6596 | 0.99982 | -0.062402 |  | 0 | 536.1195 |  |  | 551.7718
| 40626.5921 | 59.98 | 549.7406 |  |  | 550 | 0.55322 | 0.94176 | -0.048001 |  | 0 | 536.0614 |  |  | 551.7718
| 40626.5921 | 59.984 | 549.7406 |  |  | 550 | 0 | 0.81933 | -0.038397 |  | 0 | 535.939 |  |  | 551.7718
| 40626.5921 | 59.988 | 550.2887 |  |  | 550 | 0 | 0.71282 | -0.028802 |  | 0 | 535.8325 |  |  | 551.7718
| 40626.5921 | 59.992 | 550.2887 |  |  | 550 | 0 | 0.62015 | -0.019199 |  | 0 | 535.7398 |  |  | 551.7718
| 40626.5922 | 59.997 | 549.5185 |  |  | 550 | 0 | 0.53953 | -0.007196 |  | 0 | 535.6592 |  |  | 551.7718
| 40626.5922 | 60.003 | 549.5185 |  |  | 550 | 0 | 0.46939 | 0.007196 |  | 0 | 535.589 |  |  | 551.7718
| 40626.5922 | 60.007 | 549.0308 |  |  | 550 | 0 | 0.40837 | 0.0168 |  | 0 | 535.528 |  |  | 551.7718
| 40626.5922 | 60.01 | 549.0308 |  |  | 550 | 0 | 0.35528 | 0.023996 |  | 0 | 535.4749 |  |  | 551.7718
| 40626.5922 | 60.013 | 549.8664 |  |  | 550 | 0 | 0.3091 | 0.031201 |  | 0 | 535.4287 |  |  | 551.7718
| 40626.5923 | 60.015 | 549.8664 |  |  | 550 | 0 | 0.26891 | 0.035999 |  | 0 | 535.3886 |  |  | 551.7718
| 40626.5923 | 60.018 | 550.1417 |  |  | 550 | -0.18467 | 0.20995 | 0.043204 |  | 0 | 535.3296 |  |  | 551.7718
| 40626.5923 | 60.022 | 550.1417 |  |  | 550 | -0.92177 | 0.062825 | 0.052798 |  | 0 | 535.1825 |  |  | 551.7718
| 40626.5923 | 60.026 | 550.1417 |  |  | 550 | -1.6596 | -0.16109 | 0.062402 |  | 0 | 534.9585 |  |  | 551.7718
| 40626.5924 | 60.025 | 550.1417 |  |  | 550 | -1.4753 | -0.33194 | 0.060004 |  | 0 | 534.7877 |  |  | 551.7718
| 40626.5924 | 60.024 | 548.872 |  |  | 550 | -1.2903 | -0.45653 | 0.057596 |  | 0 | 534.6631 |  |  | 551.7718
| 40626.5924 | 60.02 | 548.872 |  |  | 550 | -0.55322 | -0.4691 | 0.048001 |  | 0 | 534.6505 |  |  | 551.7718
| 40626.5924 | 60.02 | 549.1459 |  |  | 550 | -0.55322 | -0.48003 | 0.048001 |  | 0 | 534.6396 |  |  | 551.7718
| 40626.5925 | 60.02 | 549.1459 |  |  | 550 | -0.55322 | -0.48955 | 0.048001 |  | 0 | 534.6301 |  |  | 551.7718
| 40626.5925 | 60.032 | 549.5798 |  |  | 550 | -2.7659 | -0.78548 | 0.076804 |  | 0 | 534.3342 |  |  | 551.7718
| 40626.5925 | 60.034 | 549.5798 |  |  | 550 | -3.1345 | -1.0909 | 0.081601 |  | 0 | 534.0288 |  |  | 551.7718
| 40626.5925 | 60.031 | 550.1505 |  |  | 550 | -2.581 | -1.2846 | 0.074396 |  | 0 | 533.8351 |  |  | 551.7718
| 40626.5925 | 60.031 | 550.1505 |  |  | 550 | -2.581 | -1.4531 | 0.074396 |  | 0 | 533.6665 |  |  | 551.7718
| 40626.5926 | 60.037 | 548.9629 |  |  | 550 | -3.6873 | -1.7435 | 0.088797 |  | 0 | 533.3761 |  |  | 551.7718
| 40626.5926 | 60.044 | 548.9629 |  |  | 550 | -4.978 | -2.164 | 0.1056 |  | 0 | 532.9556 |  |  | 551.7718
| 40626.5926 | 60.039 | 548.272 |  |  | 550 | -4.0566 | -2.4101 | 0.093604 |  | 0 | 532.7096 |  |  | 551.7718
| 40626.5926 | 60.037 | 548.272 |  |  | 550 | -3.6873 | -2.5761 | 0.088797 |  | 0 | 532.5435 |  |  | 551.7718
| 40626.5927 | 60.038 | 545.4987 |  |  | 550 | -3.8716 | -2.7445 | 0.091196 |  | 0 | 532.3751 |  |  | 551.7718
| 40626.5927 | 60.039 | 545.4987 |  |  | 550 | -4.0566 | -2.9151 | 0.093604 |  | 0 | 532.2045 |  |  | 551.7718
| 40626.5927 | 60.039 | 544.7425 |  |  | 550 | -4.0566 | -3.0635 | 0.093604 |  | 0 | 532.0562 |  |  | 551.7718
| 40626.5927 | 60.044 | 544.7425 |  |  | 550 | -4.978 | -3.3124 | 0.1056 |  | 0 | 531.8073 |  |  | 551.7718
| 40626.5928 | 60.04 | 544.7425 |  |  | 550 | -4.2409 | -3.4331 | 0.096002 |  | 0 | 531.6866 |  |  | 551.7718
| 40626.5928 | 60.036 | 545.0195 |  |  | 550 | -3.5031 | -3.4422 | 0.086398 |  | 0 | 531.6775 |  |  | 551.7718
| 40626.5928 | 60.034 | 545.4091 |  |  | 550 | -3.1345 | -3.4022 | 0.081601 |  | 0 | 531.7175 |  |  | 551.7718
| 40626.5928 | 60.034 | 545.4091 |  |  | 550 | -3.1345 | -3.3674 | 0.081601 |  | 0 | 531.7523 |  |  | 551.7718
| 40626.5928 | 60.035 | 545.2927 |  |  | 550 | -3.3188 | -3.3611 | 0.084 |  | 0 | 531.7586 |  |  | 551.7718
| 40626.5929 | 60.036 | 545.2927 |  |  | 550 | -3.5031 | -3.3795 | 0.086398 |  | 0 | 531.7401 |  |  | 551.7718
| 40626.5929 | 60.035 | 546.0543 |  |  | 550 | -3.3188 | -3.3716 | 0.084 |  | 0 | 531.748 |  |  | 551.7718
| 40626.5929 | 60.036 | 546.0543 |  |  | 550 | -3.5031 | -3.3887 | 0.086398 |  | 0 | 531.7309 |  |  | 551.7718
| 40626.5929 | 60.041 | 545.269 |  |  | 550 | -4.4251 | -3.5234 | 0.098401 |  | 0 | 531.5962 |  |  | 551.7718
| 40626.593 | 60.046 | 545.269 |  |  | 550 | -5.3472 | -3.7605 | 0.1104 |  | 0 | 531.3591 |  |  | 551.7718
| 40626.593 | 60.043 | 544.9313 |  |  | 550 | -4.7937 | -3.8948 | 0.1032 |  | 0 | 531.2248 |  |  | 551.7718
| 40626.593 | 60.037 | 544.9313 |  |  | 550 | -3.6873 | -3.8679 | 0.088797 |  | 0 | 531.2518 |  |  | 551.7718
| 40626.593 | 60.036 | 544.9313 |  |  | 550 | -3.5031 | -3.8204 | 0.086398 |  | 0 | 531.2992 |  |  | 551.7718
| 40626.5931 | 60.034 | 544.0342 |  |  | 550 | -3.1345 | -3.7313 | 0.081601 |  | 0 | 531.3884 |  |  | 551.7718
| 40626.5931 | 60.034 | 542.7912 |  |  | 550 | -3.1345 | -3.6537 | 0.081601 |  | 0 | 531.4659 |  |  | 551.7718
| 40626.5931 | 60.037 | 542.7912 |  |  | 550 | -3.6873 | -3.6581 | 0.088797 |  | 0 | 531.4616 |  |  | 551.7718
| 40626.5931 | 60.035 | 542.7912 |  |  | 550 | -3.3188 | -3.614 | 0.084 |  | 0 | 531.5057 |  |  | 551.7718
| 40626.5931 | 60.031 | 545.318 |  |  | 550 | -2.581 | -3.4797 | 0.074396 |  | 0 | 531.64 |  |  | 551.7718
Note on H1: If "Auto" event detection is selected (default), observe the "Initial & Sustained Graph" and adjust graph alignment per instructions on that worksheet. If Manual is selected, determine beginning of event by observing frequency on the "Data" worksheet and enter the row number of the desired event's first change in frequency. Enter this row number in cell H2.
Note on H3: If "Manual" event detection is selected, observe frequency following the beginning of the event. When actual frequency recovers to 60.00 Hz minus the governor deadband for low frequency events or plus the governor deadband for high frequency events, enter that row number in this cell. If Auto was selected, no action is required, this cell value is not used.
Note on M10: Enter the MW value where the steam generator typically reaches rated pressure. If pressure is constant for the normal operating range enter the same value as is entered as the Governor minimum operating level.
Note on O10: Enter up to four additional midrange breakpoints if needed. In not needed, enter same values as the Pressure PSI (1) and MW (1).
Note on M11: Enter the MW value where the steam generator typically reaches minimum pressure.
Note on L13: TC allowable range 0.050 to 1.000 with 1.0 turning filter off. Beginning Target MW slope on the "Model Period Graph" should align with the Actual MW slope. Increasing the value of the TC causes the Target to change with frequency quicker.

## Summary
|  | Governor and Evaluation Settings | [5 empty] | Headroom and Margin |  |  |  | Event Frequency and Time |  |  |  | Resource Data - Initial Measure: R9 | [8 empty] | Resource Data - Sustained Measure :R10
[18 empty] | Delta MW | Expected | Initial | Initial | Initial | Throttle | Expected Primary | Net MW | Actual Output | Target | Sustained
Date | Generator | Net |  | Governor | Governor | K (Limiting Factor) | TC | Frequency | Up | Down | Is EPFR (final) | A Value | t(0) Time | B Value | Delta Hz | A Value | B Value | B Value | Primary | Performance | Performance | Performance | Pressure | Frequency Response | Change During | Relative | Relative | Performance
of Event |  | Dependable | Power | Droop | Dead-band | PSI Change/MW Change | Time Constant | Responsive | Headroom | Headroom | Margin | Hz |  | Hz | B Value | t(-2) to t(-16) | t(+20) to t(+52) | minus | Frequency | P.U. | Ramp Magnitude | Stm Flow & | % of Rated | Based on | Event Recovery | Average | Average | P.U.
|  | Capability | Augmentation | Evaluation | Evaluation |  |  | HSL |  |  | Available | t(-2) to t(-16) | hh:mm:ss | t(+20) to t(+52) | minus |  |  | A Value | Response Final |  | Adjustment | Stored Energy Adj |  | Droop and Dead-band | Period | Change | Change
|  | MW | MW | % | Hz |  |  | MW | % of HSL | % of HSL | Yes/No |  |  |  | A Value | MW | MW | MW | MW |  | MW | MW | % | MW | MW | MW | MW
2011-03-24 13:59 | Unit:Generator x | 550 | 0 | 5% | 0.017 | 0.24 | 0.13 | 550 | 3.615% | 70.93% | No | 60.0024 | 40626.5827 | 59.8206 | -0.18179 | 530.1148 | 543.7391 | 16.4944 | 26.6887 | 0.75 | -2.8701 | -3.2565 | 100% | 29.9451 | 20.6134 | -3.3822 | 30.9758 | 0.75

## Instructions
Instructions for using this spreadsheet.
Initial setup for the specific generator. All entries on the "Evaluation" spreadsheet.
Enter Generator name in cell K1.
Enter Generator turbine Net Dependable Capability in Cell L3.
Droop Setting in cell L4 should be 5.0 %.
Dead-band Setting in cell L5 should be the maximum allowed for the type of governor; mechanical or electrical or digital.
Enter Governor type in cell L7.
Enter Rated Steam Pressure of the turbine in cell L10. If operation utilizes over-pressure, enter the normal over-pressure value utilized.
Enter nominal MW output when attaining the operating pressure stated in cell L10.
The evaluation considers up to five throttle pressure breakpoints that can be utilizied. Enter the Pressure breakpoint in cells O10, R10, U10, X10 and minimum L11.
Enter the corresponding MW value that occurs when each of these Pressure breakpoints are attained in the corresponding adjacent cell.
If all the breakpoints are not needed just repeat the entries.
Enter the K (Limiting Factor). This value is based on observed changes in throttle pressure immediately following a significant disturbance and the turbine responds correctly.
Observe the change in throttle pressure as a ratio to the MW change and enter that ratio in cell L12. The ratio should be between 0 and 0.6.
Enter Time Constant (TC) in cell L13 that models the delay in delivery of frequency response. This value should be no lower than 0.050 and no greater than 1.0. (Not part of the standard measure, only the Model Target).
The appropriate TC can be observed on the Model Period Graph. The "Target" trend should respond similar to the actual MW response. To slow down the target, reduce the TC.
Enter the maximum operating output of the generator in cell L15, HSL.
Enter the minimum operating output of the generator in cell L16, LSL.
Once each of these steps are completed, save the workbook as a master workbook for this generator.
For each frequency event evaluated, follow these additional steps.
Collect 2 second data of frequency and MW output of the generator. Provide time in the hh:mm:ss format. Add this data to the "Data" worksheet in columns A6..C1806 for Time, Frequency and MW.
The spreadsheet is setup for 60 minutes of data however, less data may be used. You must start the data at least two minutes before the start of the event. Erase all unused data in the unused area of the Data worksheet including formulas in columns O through S.
With "Auto" selected on the "Evaluation" worksheet in cell H1, observe the "Initial & Sustained Graph" worksheet and adjust the frequency data alignment as instructed on that worksheet.
Evaluation should be complete with P.U. performance data provided on the Initial & Sustained Graph, the Evaluation worksheet and summarized on the Summary worksheet.
The Model Period Graph is for observation only and is not part of the BAL-001-TRE regional standard.
You can create a Resource "Summary" workbook by copying the results on the Summary worksheet to a Summary workbook. Do this for each event evaluated for this generator and create a rolling average performance.